SEE-Tech Solutions

# Detailed Energy Audit Report

M/S VR DAKSHIN PRIVATE LIMITED

Commercial Mall / Retail Building

Audit Period:

Prepared By: SEE-Tech Solutions

# 1. Executive Summary

| Particular | Value |
| --- | --- |
| Facility name | M/S VR DAKSHIN PRIVATE LIMITED |
| Building type | Commercial Mall / Retail Building |
| Service number | 019094061918 |
| Contract demand | 7,000 kVA |
| Tariff | HT III / HT III |
| Supply voltage | 33 kV |
| Annual kWh | 2,17,82,502 kWh |
| Annual electricity cost | ₹28,65,88,021 |
| Average tariff | ₹13/kWh |
| ECM count | 14 |
| Total energy saving | 29,35,731 kWh/year |
| Total annual saving | ₹3,95,44,302 |
| Total investment | ₹2,70,55,427 |
| Overall payback, years | 0.68 years |
| Overall payback, months | 8.21 months |

# 2. Facility and Billing Profile

| Particular | Value |
| --- | --- |
| Client name | M/S VR DAKSHIN PRIVATE LIMITED |
| Facility name | M/S VR DAKSHIN PRIVATE LIMITED |
| Address | NO .44,PILLAYAR KOIL STREETJAWAHARLAL NEHRU SALAI,THIRUMANGALABEHIND VEE CARE HOSPITAL CHENNAI - 600 040 |
| Building type | Commercial Mall / Retail Building |
| Prepared by | SEE-Tech Solutions |
| Service number | 019094061918 |
| Tariff | HT III / HT III |
| Contract demand | 7,000 kVA |
| Permitted MD | 7,000 kVA |
| Supply voltage | 33 kV |
| Average power factor | 0.983 |

## Monthly Billing Summary

| Month | kWh | kVAh | Maximum Demand kVA | PF | Bill Amount Rs | Average Tariff Rs/kWh |
| --- | --- | --- | --- | --- | --- | --- |
| Feb 2025 | 16,30,305 kWh | 16,35,278 kVAh | 4,200 kVA | 0.997 | ₹2,14,55,083 | ₹13/kWh |
| Mar 2025 | 18,34,463 kWh | 5,55,765 kVAh | 4,425 kVA | 0.995 | ₹2,31,10,905 | ₹13/kWh |
| Apr 2025 | 18,62,685 kWh | 18,93,810 kVAh | 4,755 kVA | 0.984 | ₹2,45,41,621 | ₹13/kWh |
| May 2025 | 19,40,333 kWh | 19,78,665 kVAh | 4,718 kVA | 0.981 | ₹2,47,66,581 | ₹13/kWh |
| Jun 2025 | 18,12,623 kWh | 18,50,250 kVAh | 4,628 kVA | 0.98 | ₹2,34,31,316 | ₹13/kWh |
| Jul 2025 | 18,88,688 kWh | 19,31,760 kVAh | 4,650 kVA | 0.978 | ₹2,50,20,074 | ₹13/kWh |
| Aug 2025 | 19,40,888 kWh | 19,83,443 kVAh | 4,695 kVA | 0.979 | ₹2,55,98,144 | ₹13/kWh |
| Sep 2025 | 18,14,865 kWh | 18,51,900 kVAh | 4,710 kVA | 0.98 | ₹2,42,15,435 | ₹13/kWh |
| Oct 2025 | 18,82,658 kWh | 19,17,615 kVAh | 4,553 kVA | 0.982 | ₹2,49,40,585 | ₹13/kWh |
| Nov 2025 | 17,53,433 kWh | 17,83,290 kVAh | 4,523 kVA | 0.983 | ₹2,34,94,143 | ₹13/kWh |
| Dec 2025 | 17,27,423 kWh | 17,55,540 kVAh | 4,425 kVA | 0.984 | ₹2,31,97,403 | ₹13/kWh |
| Jan 2026 | 16,94,138 kWh | 17,27,108 kVAh | 4,223 kVA | 0.981 | ₹2,28,16,731 | ₹13/kWh |

# 3. Major Energy Consuming Systems

| System | Quantity | Connected Load kW | Annual Consumption kWh/year | Share % | Remarks |
| --- | --- | --- | --- | --- | --- |
| Chiller | 3 | 1,052.96 kW | 54,48,824 kWh/year | 59.74% | Counted from 3 equipment rows |
| Condenser Pump | 3 | 148.01 kW | 6,41,827 kWh/year | 7.04% | Counted from 3 equipment rows |
| Secondary CHW Pump | 4 | 77.38 kW | 4,23,153 kWh/year | 4.64% | Counted from 4 equipment rows |
| Primary CHW Pump | 4 | 91.77 kW | 4,17,223 kWh/year | 4.57% | Counted from 4 equipment rows |
| Heat Recovery Wheel fresh air | 9 | 76.22 kW | 3,89,458 kWh/year | 4.27% | Counted from 9 equipment rows |
| Scrubber | 10 | 75.29 kW | 3,29,766 kWh/year | 3.62% | Counted from 10 equipment rows |
| Escalator | 24 | 64 kW | 2,52,230 kWh/year | 2.77% | Counted from 24 equipment rows |
| AHU | 12 | 52.13 kW | 2,28,325 kWh/year | 2.5% | Counted from 12 equipment rows |
| Cooling Tower | 4 | 49.59 kW | 2,07,432 kWh/year | 2.27% | Counted from 4 equipment rows |
| Air Washer | 10 | 36.32 kW | 1,59,074 kWh/year | 1.74% | Counted from 10 equipment rows |
| CSU | 22 | 34.29 kW | 1,50,202 kWh/year | 1.65% | Counted from 22 equipment rows |
| Softener Pump | 1 | 13.81 kW | 1,20,976 kWh/year | 1.33% | Counted from 1 equipment row |
| STP Blower | 1 | 20 kW | 1,20,976 kWh/year | 1.33% | Counted from 1 equipment row |
| Heat Recovery Wheel exhaust | 9 | 17.09 kW | 87,330 kWh/year | 95.75% | Counted from 9 equipment rows |
| Office Outdoor | 2 | 12 kW | 52,566 kWh/year | 57.63% | Counted from 2 equipment rows |
| Domestic Pump | 2 | 4.96 kW | 32,604 kWh/year | 35.75% | Counted from 2 equipment rows |
| Lift | 10 | 7.19 kW | 30,708 kWh/year | 33.67% | Counted from 10 equipment rows |
| Flush Pump | 2 | 4.86 kW | 21,278 kWh/year | 23.33% | Counted from 2 equipment rows |
| FCU | 10 | 1.08 kW | 4,720 kWh/year | 5.17% | Counted from 10 equipment rows |
| Irrigation Pump | 1 | 3 kW | 2,189 kWh/year | 2.4% | Counted from 1 equipment row |

# 4. ECM Summary

| ECM No. | Project Title | System | Energy Saving kWh/year | Annual Saving Rs/year | Investment Rs | Payback, months |
| --- | --- | --- | --- | --- | --- | --- |
| ECM 1 | Contract Demand Optimization | Electrical Billing / Demand Management | 7,79,973 kWh/year | ₹1,05,06,240 | ₹2,00,000 | 0.23 months |
| ECM 2 | Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement | Cooling Tower / Chiller Condenser System | 2,72,441 kWh/year | ₹36,69,783 | ₹24,00,000 | 7.85 months |
| ECM 3 | Cooling tower motor retrofit with high efficiency PMS motor wirh VFD and automation | Cooling Tower Fan System | 38,420 kWh/year | ₹5,17,523 | ₹17,50,000 | 40.58 months |
| ECM 4 | Increase the set point of chiller as the return water is 9.4 deg C and delta t is 2.9 deg c (chilled water supply is 6.5 deg c) | Chiller Plant Controls / CHW Set Point | 2,17,953 kWh/year | ₹29,35,826 | ₹10,00,000 | 4.09 months |
| ECM 5 | Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand | Chiller Plant Automation and Sequencing | 8,56,615 kWh/year | ₹1,15,38,605 | ₹60,00,000 | 6.24 months |
| ECM 6 | Condenser pump motor refrofit with high efficiency motor (IE4/IE5) with VFD and delta t & delta p automation | Condenser Water Pumping System | 60,366 kWh/year | ₹8,13,133 | ₹15,93,000 | 23.51 months |
| ECM 7 | Primary pump motor refrofit with high efficiency motor IE5 with VFD and delta t & delta p automation | Primary CHW Pumping System | 47,997 kWh/year | ₹6,46,523 | ₹13,50,000 | 25.06 months |
| ECM 8 | Secondary pump motor refrofit with high efficiency motor IE5 with existing VFD and delta t & delta p automation | Secondary CHW Pumping System | 45,745 kWh/year | ₹6,16,181 | ₹14,25,000 | 27.75 months |
| ECM 9 | Existing IE2 efficiency class retrofit with high efficieny motor (IE5) and cogged belt | STP Blower / Motor Drive System | 17,520 kWh/year | ₹2,35,994 | ₹4,00,000 | 20.34 months |
| ECM 10 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | AHU Plug Fan System | 91,330 kWh/year | ₹12,30,215 | ₹27,82,546 | 27.14 months |
| ECM 11 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Air Washer Plug Fan System | 63,630 kWh/year | ₹8,57,091 | ₹23,13,031 | 32.38 months |
| ECM 12 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Heat Recovery Wheel / Ventilation Fan System | 1,78,858 kWh/year | ₹24,09,217 | ₹36,41,850 | 18.14 months |
| ECM 13 | Scrubber motor retrofit with high efficiency motor with VFD and DCV automation | Scrubber Ventilation Motor System | 82,442 kWh/year | ₹11,10,487 | ₹22,00,000 | 23.77 months |
| ECM 18 | Energy Saving in Chiller by improving operational practices | Chiller Operational Practice Improvement | 1,82,441 kWh/year | ₹24,57,483 | ₹0 | 0 months |

# 5. Group-wise ECM Summary

| Group | ECM Count | Energy Saving kWh/year | Annual Saving Rs/year | Investment Rs | Payback, years |
| --- | --- | --- | --- | --- | --- |
| GR-1 Electrical Billing and Demand Optimization | 1 | 7,79,973 kWh/year | ₹1,05,06,240 | ₹2,00,000 | 0.02 years |
| GR-2 Chiller Plant and Cooling Tower Optimization | 5 | 15,67,871 kWh/year | ₹2,11,19,220 | ₹1,11,50,000 | 0.53 years |
| GR-3 Pumping System Optimization | 3 | 1,54,108 kWh/year | ₹20,75,837 | ₹43,68,000 | 2.1 years |
| GR-4 Air Handling, Ventilation and Blower Optimization | 5 | 4,33,779 kWh/year | ₹58,43,004 | ₹1,13,37,427 | 1.94 years |

# 6. Detailed ECM Sheets

## ECM 1: Contract Demand Optimization

| Particular | Value |
| --- | --- |
| ECM No. | ECM 1 |
| Project title | Contract Demand Optimization |
| System | Electrical Billing / Demand Management |
| Equipment covered | Meter |
| Baseline kWh/year |  |
| Saving % | 3.58% |
| Energy saving kWh/year | 7,79,973 kWh/year |
| Annual saving Rs/year | ₹1,05,06,240 |
| Investment Rs | ₹2,00,000 |
| Payback, months | 0.23 months |
| Payback, years | 0.02 years |

### Existing Condition

Meter. Monthly Recorded Maximum Demand (kVA) 1. Feb 2025 – 4200 kVA 2. Mar 2025 – 4425 kVA 3. Apr 2025 – 4755 kVA (highest) 4. May 2025 – 4718 kVA 5. Jun 2025 – 4628 kVA 6. Jul 2025 – 4650 kVA 7. Aug 2025 – 4695 kVA 8. Sep 2025 – 4710 kVA 9. Oct 2025 – 4553 kVA 10. Nov 2025 – 4523 kVA 11. Dec 2025 – 4425 kVA 12. Jan 2026 – 4223 kVA Average: 4542 kVA

### Problem / Gap

Since the highest MD recorded in April 2025 is 4755 kVA, there is a strong opportunity to optimize the contract demand and avoid unnecessary demand charges from the utility

### Proposed Project

Contract Demand Optimization. This project optimizes contract demand based on actual Maximum Demand of 4755 kVA recorded in April 2025. The proposed demand is 5400 kVA, providing a safe margin while reducing unnecessary charges. It helps lower electricity costs, control peak demand, and improve efficiency without affecting operations

### Project Activities

- Collect historical MD data (15-min interval) from energy meter 2. Analyze monthly peak demand trends 3. Identify peak load conditions and timings

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year |  |
| Saving % | 3.58% |
| Energy saving kWh/year | 7,79,973 kWh/year |
| Annual saving Rs/year | ₹1,05,06,240 |
| Investment Rs | ₹2,00,000 |
| Payback, months | 0.23 months |
| Payback, years | 0.02 years |

### M&V Plan

- Compare monthly recorded demand and billed demand before and after contract demand revision.

- Verify demand charge reduction from utility bills.

- Confirm no demand penalty occurs after revision.

### Benefits

- Reduces energy use in the Electrical Billing / Demand Management system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 1 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 2: Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement

| Particular | Value |
| --- | --- |
| ECM No. | ECM 2 |
| Project title | Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement |
| System | Cooling Tower / Chiller Condenser System |
| Equipment covered | Cooling Tower 2 & 3 |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 5% |
| Energy saving kWh/year | 2,72,441 kWh/year |
| Annual saving Rs/year | ₹36,69,783 |
| Investment Rs | ₹24,00,000 |
| Payback, months | 7.85 months |
| Payback, years | 0.65 years |

### Existing Condition

Cooling Tower 2 & 3. Detailed existing condition is not available in uploaded data and is listed in Annexure B for site verification.

### Problem / Gap

Cooling tower approach is high, causing the chiller condenser cooling water temperature to reach (WBT + 5°C), which is excessive and resulting in higher chiller power consumption

### Proposed Project

Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement. Reducing the cooling tower approach by optimizing fan blade angle and damaged fins replacement improves heat rejection efficiency, which lowers condenser water temperature. This reduces chiller compressor load and power consumption, resulting in energy savings, improved system performance (For every 1°C reduction in condenser water temperature, the chiller compressor power consumption decreases by approximately 2% to 3%).

### Project Activities

- Measurement of existing cooling tower performance (approach, temperature, power).

- Analysis of fan blade angle and airflow condition.

- Optimization/adjustment of fan blade angle.

- Replacement of damaged fins by new one.

- Measurement of power consumption before and after implementation.

- Calculation and verification of energy savings.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 5% |
| Energy saving kWh/year | 2,72,441 kWh/year |
| Annual saving Rs/year | ₹36,69,783 |
| Investment Rs | ₹24,00,000 |
| Payback, months | 7.85 months |
| Payback, years | 0.65 years |

### M&V Plan

- Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.

- Compare kW/TR before and after implementation.

- Normalize comparison for cooling load and operating hours.

### Benefits

- Reduces energy use in the Cooling Tower / Chiller Condenser System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 2 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 3: Cooling tower motor retrofit with high efficiency PMS motor wirh VFD and automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 3 |
| Project title | Cooling tower motor retrofit with high efficiency PMS motor wirh VFD and automation |
| System | Cooling Tower Fan System |
| Equipment covered | Cooling Tower 2 & 3 |
| Baseline kWh/year | 1,92,102 kWh/year |
| Saving % | 20% |
| Energy saving kWh/year | 38,420 kWh/year |
| Annual saving Rs/year | ₹5,17,523 |
| Investment Rs | ₹17,50,000 |
| Payback, months | 40.58 months |
| Payback, years | 3.38 years |

### Existing Condition

Cooling Tower 2 & 3. Cooling Tower 2 & 3 Motor Specifictaions (7.5 kW x 4 Nos, 570 RPM, Direct Driven CT Fan, Flange, Frame 180 MV

### Problem / Gap

IE2 Efficiency class motor to be changed with IE5 Efficiency class motor

### Proposed Project

Cooling tower motor retrofit with high efficiency PMS motor wirh VFD and automation. Upgrade CT-2 & CT-3 motors from IE2 to high-efficiency IE5 PMS motors with VFD and automation to optimize fan speed as per demand. This reduces energy consumption and improves system efficiency, with expected savings of 15–20%

### Project Activities

- Replacement of existing IE2 motors with IE5 PMS motors for CT-2 & CT-3.

- Installation and commissioning of VFDs for cooling tower fans.

- Implementation of See-Condensync system for cooling tower performance improvement automation.

- Integration of automation system with cooling tower and chiller operation.

- Monitoring of condenser water temperature and chiller load through See-Condensync.

- Testing, optimization, and performance validation of the system.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 1,92,102 kWh/year |
| Saving % | 20% |
| Energy saving kWh/year | 38,420 kWh/year |
| Annual saving Rs/year | ₹5,17,523 |
| Investment Rs | ₹17,50,000 |
| Payback, months | 40.58 months |
| Payback, years | 3.38 years |

### M&V Plan

- Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.

- Compare kW/TR before and after implementation.

- Normalize comparison for cooling load and operating hours.

### Benefits

- Reduces energy use in the Cooling Tower Fan System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 3 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 4: Increase the set point of chiller as the return water is 9.4 deg C and delta t is 2.9 deg c (chilled water supply is 6.5 deg c)

| Particular | Value |
| --- | --- |
| ECM No. | ECM 4 |
| Project title | Increase the set point of chiller as the return water is 9.4 deg C and delta t is 2.9 deg c (chilled water supply is 6.5 deg c) |
| System | Chiller Plant Controls / CHW Set Point |
| Equipment covered | Chiller |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 4% |
| Energy saving kWh/year | 2,17,953 kWh/year |
| Annual saving Rs/year | ₹29,35,826 |
| Investment Rs | ₹10,00,000 |
| Payback, months | 4.09 months |
| Payback, years | 0.34 years |

### Existing Condition

Chiller. Return water = 9.4°C, Supply water = 6.5°C, Delta-T = 2.9°C. Indicates opportunity to optimize set point and improve efficiency

### Problem / Gap

Specific problem statement is not available in uploaded data and is listed in Annexure B.

### Proposed Project

Increase the set point of chiller as the return water is 9.4 deg C and delta t is 2.9 deg c (chilled water supply is 6.5 deg c). Raising chilled water supply temperature improves chiller COP/efficiency and reduces compressor power consumption. No major capital cost. Quick payback.

### Project Activities

- Analyze process cooling requirement, verify comfort/process limits, gradually increase set point, monitor return temp, delta-T, kW/TR, and room/process conditions.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 4% |
| Energy saving kWh/year | 2,17,953 kWh/year |
| Annual saving Rs/year | ₹29,35,826 |
| Investment Rs | ₹10,00,000 |
| Payback, months | 4.09 months |
| Payback, years | 0.34 years |

### M&V Plan

- Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.

- Compare kW/TR before and after implementation.

- Normalize comparison for cooling load and operating hours.

### Benefits

- Reduces energy use in the Chiller Plant Controls / CHW Set Point system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 4 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 5: Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand

| Particular | Value |
| --- | --- |
| ECM No. | ECM 5 |
| Project title | Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand |
| System | Chiller Plant Automation and Sequencing |
| Equipment covered | Chiller Plant Manager |
| Baseline kWh/year | 71,38,459 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 8,56,615 kWh/year |
| Annual saving Rs/year | ₹1,15,38,605 |
| Investment Rs | ₹60,00,000 |
| Payback, months | 6.24 months |
| Payback, years | 0.52 years |

### Existing Condition

Chiller Plant Manager. 1. 1000 TR Centrifugal Chiller (Mall) x 3 Nos. (Without VFD) 2. 500 TR Centrifugal Chiller (Cinema) x 1 No. (Without VFD) 3. 1629 TR Cooling Tower (Mall) x 3 Nos. (Without VFD) 4. 676 TR Cooling Tower (Cinema) x 1 No. (Without VFD) 5. 30 kW Primary Pump (Mall) x 4 Nos. (Without VFD) 6. 15 kW Primary Pump (Cinema) x 2 Nos. (Without VFD) 7. 37 kW Seconadry Pump (Mall) x 5 Nos. (With VFD) 8. 22 kW Seconadry Pump (Cinema) x 2 Nos. (With VFD) 9. 75 kW Condenser Pump (Mall) x 4 Nos. (Without VFD) 10. 30 kW Condenser Pump (Cinema) x 2 Nos. (Without VFD) Additional Notes: Put VFDs on all pumps, motors and sensor along with chiller controller

### Problem / Gap

Cooling load varies significantly across summer, monsoon, winter seasons and process demand. Existing system operates with fixed-speed chillers, cooling towers and primary pumps, resulting in part-load inefficiencies, excess pumping power and sub-optimal condenser pressure control.

### Proposed Project

Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand. Reduces overall chiller plant kW/TR through intelligent automation, optimized equipment sequencing, dynamic setpoint control, condenser optimization and demand-based pumping operation. Improves system stability, reduces over-pumping and enhances part-load performance.

### Project Activities

- Detailed engineering study, installation of flow meters, pressure/temperature sensors, PLC/BMS integration, automated chiller sequencing logic, condenser water optimization logic, pump optimization, communication integration with chillers, testing, commissioning and operator training.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 71,38,459 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 8,56,615 kWh/year |
| Annual saving Rs/year | ₹1,15,38,605 |
| Investment Rs | ₹60,00,000 |
| Payback, months | 6.24 months |
| Payback, years | 0.52 years |

### M&V Plan

- Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.

- Compare kW/TR before and after implementation.

- Normalize comparison for cooling load and operating hours.

### Benefits

- Reduces energy use in the Chiller Plant Automation and Sequencing system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 5 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 18: Energy Saving in Chiller by improving operational practices

| Particular | Value |
| --- | --- |
| ECM No. | ECM 18 |
| Project title | Energy Saving in Chiller by improving operational practices |
| System | Chiller Operational Practice Improvement |
| Equipment covered | Chiller |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 5% |
| Energy saving kWh/year | 1,82,441 kWh/year |
| Annual saving Rs/year | ₹24,57,483 |
| Investment Rs | ₹0 |
| Payback, months | 0 months |
| Payback, years | 0 years |

### Existing Condition

Chiller. Detailed existing condition is not available in uploaded data and is listed in Annexure B for site verification.

### Problem / Gap

Cooling tower approach is high, causing the chiller condenser cooling water temperature to reach (WBT + 5°C), which is excessive and resulting in higher chiller power consumption

### Proposed Project

Energy Saving in Chiller by improving operational practices. 1. Use 2 CTs for 1 Chiller 2. Use 3 CTs for 2 Chiller 3. Use 4 CTs for 3 Chiller (For every 1°C reduction in condenser water temperature, the chiller compressor power consumption decreases by approximately 2% to 3%).

### Project Activities

- By operating additional CT, power consumption increases by 90,000 kWh/Year and water consumption increases by 190 to 200 kL/day but saving is huge in Chiller, this all points incorporated

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 54,48,824 kWh/year |
| Saving % | 5% |
| Energy saving kWh/year | 1,82,441 kWh/year |
| Annual saving Rs/year | ₹24,57,483 |
| Investment Rs | ₹0 |
| Payback, months | 0 months |
| Payback, years | 0 years |

### M&V Plan

- Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.

- Compare kW/TR before and after implementation.

- Normalize comparison for cooling load and operating hours.

### Benefits

- Reduces energy use in the Chiller Operational Practice Improvement system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 18 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 6: Condenser pump motor refrofit with high efficiency motor (IE4/IE5) with VFD and delta t & delta p automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 6 |
| Project title | Condenser pump motor refrofit with high efficiency motor (IE4/IE5) with VFD and delta t & delta p automation |
| System | Condenser Water Pumping System |
| Equipment covered | Condenser Pump 1 & 3 |
| Baseline kWh/year | 6,03,662 kWh/year |
| Saving % | 10% |
| Energy saving kWh/year | 60,366 kWh/year |
| Annual saving Rs/year | ₹8,13,133 |
| Investment Rs | ₹15,93,000 |
| Payback, months | 23.51 months |
| Payback, years | 1.96 years |

### Existing Condition

Condenser Pump 1 & 3. Detailed existing condition is not available in uploaded data and is listed in Annexure B for site verification.

### Problem / Gap

Cooling Load significantly varrying with season and variation in cooling requirement

### Proposed Project

Condenser pump motor refrofit with high efficiency motor (IE4/IE5) with VFD and delta t & delta p automation. Upgrade the condenser pump motor with a high-efficiency IE4/IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 4–6%.

### Project Activities

- IE5 Efficiency class motor with VFD and automation (75 kW, 4 Pole, Mounting: foot, frame size: 280S

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 6,03,662 kWh/year |
| Saving % | 10% |
| Energy saving kWh/year | 60,366 kWh/year |
| Annual saving Rs/year | ₹8,13,133 |
| Investment Rs | ₹15,93,000 |
| Payback, months | 23.51 months |
| Payback, years | 1.96 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| Condenser pump | ₹11,88,175 |

### M&V Plan

- Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.

- Compare before/after kW under similar load.

- Verify stable flow or pressure after control changes.

### Benefits

- Reduces energy use in the Condenser Water Pumping System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 6 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 7: Primary pump motor refrofit with high efficiency motor IE5 with VFD and delta t & delta p automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 7 |
| Project title | Primary pump motor refrofit with high efficiency motor IE5 with VFD and delta t & delta p automation |
| System | Primary CHW Pumping System |
| Equipment covered | Primary Pump 1, 2 & 3 |
| Baseline kWh/year | 3,99,977 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 47,997 kWh/year |
| Annual saving Rs/year | ₹6,46,523 |
| Investment Rs | ₹13,50,000 |
| Payback, months | 25.06 months |
| Payback, years | 2.09 years |

### Existing Condition

Primary Pump 1, 2 & 3. Detailed existing condition is not available in uploaded data and is listed in Annexure B for site verification.

### Problem / Gap

Cooling Load significantly varrying with season and variation in cooling requirement

### Proposed Project

Primary pump motor refrofit with high efficiency motor IE5 with VFD and delta t & delta p automation. Upgrade the condenser pump motor with a high-efficiency IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 10 to 12%.

### Project Activities

- IE5 Efficiency class motor with VFD and automation (30 kW, 4 Pole, Mounting: foot, frame size: 200L

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 3,99,977 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 47,997 kWh/year |
| Annual saving Rs/year | ₹6,46,523 |
| Investment Rs | ₹13,50,000 |
| Payback, months | 25.06 months |
| Payback, years | 2.09 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| Pri pump | ₹4,81,811 |

### M&V Plan

- Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.

- Compare before/after kW under similar load.

- Verify stable flow or pressure after control changes.

### Benefits

- Reduces energy use in the Primary CHW Pumping System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 7 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 8: Secondary pump motor refrofit with high efficiency motor IE5 with existing VFD and delta t & delta p automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 8 |
| Project title | Secondary pump motor refrofit with high efficiency motor IE5 with existing VFD and delta t & delta p automation |
| System | Secondary CHW Pumping System |
| Equipment covered | Secondary Pump 1, 3, & 2(C) |
| Baseline kWh/year | 3,81,206 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 45,745 kWh/year |
| Annual saving Rs/year | ₹6,16,181 |
| Investment Rs | ₹14,25,000 |
| Payback, months | 27.75 months |
| Payback, years | 2.31 years |

### Existing Condition

Secondary Pump 1, 3, & 2(C). Detailed existing condition is not available in uploaded data and is listed in Annexure B for site verification.

### Problem / Gap

Cooling Load significantly varrying with season and variation in cooling requirement

### Proposed Project

Secondary pump motor refrofit with high efficiency motor IE5 with existing VFD and delta t & delta p automation. Upgrade the condenser pump motor with a high-efficiency IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 10%.

### Project Activities

- IE5 Efficiency class motor with VFD and automation 1. 37 kW, 4 Pole, Mounting: foot, frame size: 225S 2. 22 kW, 4 Pole, Mounting: foot, frame size:180L (Cinema)

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 3,81,206 kWh/year |
| Saving % | 12% |
| Energy saving kWh/year | 45,745 kWh/year |
| Annual saving Rs/year | ₹6,16,181 |
| Investment Rs | ₹14,25,000 |
| Payback, months | 27.75 months |
| Payback, years | 2.31 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| SEC pump | ₹4,49,375 |
| SEc pump cinema | ₹3,07,684 |

### M&V Plan

- Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.

- Compare before/after kW under similar load.

- Verify stable flow or pressure after control changes.

### Benefits

- Reduces energy use in the Secondary CHW Pumping System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 8 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 9: Existing IE2 efficiency class retrofit with high efficieny motor (IE5) and cogged belt

| Particular | Value |
| --- | --- |
| ECM No. | ECM 9 |
| Project title | Existing IE2 efficiency class retrofit with high efficieny motor (IE5) and cogged belt |
| System | STP Blower / Motor Drive System |
| Equipment covered | Air Blower (STP) |
| Baseline kWh/year | 87,600 kWh/year |
| Saving % | 20% |
| Energy saving kWh/year | 17,520 kWh/year |
| Annual saving Rs/year | ₹2,35,994 |
| Investment Rs | ₹4,00,000 |
| Payback, months | 20.34 months |
| Payback, years | 1.69 years |

### Existing Condition

Air Blower (STP). IE5 Efficiency class motor with VFD (22 kW, 4 Pole, Mounting: foot, frame size: 180L

### Problem / Gap

Upgrading from an IE2 to IE5 motor significantly improves motor efficiency, reducing electrical losses. Additionally, replacing the conventional belt with a cogged belt minimizes transmission losses and slippage, ensuring better power transfer. This results in lower energy consumption and improved overall blower performance

### Proposed Project

Existing IE2 efficiency class retrofit with high efficieny motor (IE5) and cogged belt. Upgrade the existing IE2 motor to a high-efficiency IE5 motor and replace the conventional belt with a cogged belt to improve power transmission and reduce losses with DO sensors. This enhances overall blower efficiency and reduces energy consumption

### Project Activities

- Replacement of existing IE2 motor with high-efficiency IE5 motor.

- Replacement of conventional belt with cogged belt.

- Pulley inspection and alignment for efficient power transmission.

- Electrical connections and necessary panel modifications.

- Blower performance testing and load optimization.

- Monitoring and validation of energy savings.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 87,600 kWh/year |
| Saving % | 20% |
| Energy saving kWh/year | 17,520 kWh/year |
| Annual saving Rs/year | ₹2,35,994 |
| Investment Rs | ₹4,00,000 |
| Payback, months | 20.34 months |
| Payback, years | 1.69 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| Air Blower | ₹3,98,551 |

### M&V Plan

- Measure motor kW, airflow, static pressure and operating hours.

- Compare before and after fan or blower energy use.

- Verify ventilation, comfort or process requirement is maintained.

### Benefits

- Reduces energy use in the STP Blower / Motor Drive System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 9 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 10: Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 10 |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| System | AHU Plug Fan System |
| Equipment covered | Air Handling Unit (12 Nos) |
| Baseline kWh/year | 2,28,325 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 91,330 kWh/year |
| Annual saving Rs/year | ₹12,30,215 |
| Investment Rs | ₹27,82,546 |
| Payback, months | 27.14 months |
| Payback, years | 2.26 years |

### Existing Condition

Air Handling Unit (12 Nos). YEARLY AHU KWH CONSUMPTION 1. AHU 01 GF (15,000cfm@65mmwg) - 20,468 kWh/year 2. AHU 02 GF (24,000cfm@65mmwg) - 20,135 kWh/year 3. AHU 03 GF (19,000cfm@65mmwg) - 13,140 kWh/year 4. AHU 01 1F (10,000cfm@65mmwg) - 12,099 kWh/year 5. AHU 02 1F (10,000cfm@65mmwg) - 6,456 kWh/year 6. AHU 03 1F (10,000cfm@65mmwg)- 15,196 kWh/year 7. AHU 01 2F (10,000cfm@65mmwg) - 7,450 kWh/year 8. AHU 02 2F (10,000cfm@65mmwg) - 13,815 kWh/year 9. AHU 03 2F (10,000cfm@65mmwg) - 15,201 kWh/year 10. AHU 01 Terrace (22,200cfm@65mmwg) - 22,500 kWh/year 11. AHU 02 Terrace (24,000cfm@65mmwg) - 33,875 kWh/year 12.AHU 03 Terrace (22,200cfm@65mmwg) - 32,660 kWh/year

### Problem / Gap

Belt driven fan, IE2 efficincy motor

### Proposed Project

Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation. Replacement of belt-driven blowers with direct-driven aerofoil plug fans equipped with IE5 high-efficiency motors significantly reduces transmission losses and improves overall system efficiency. The elimination of belts minimizes maintenance, improves reliability, and ensures consistent airflow. Automation further optimizes energy usage by adjusting fan speed based on demand, leading to substantial power savings and improved system performance.

### Project Activities

- Selection and sizing of suitable plug fans and IE5 motors 2. Removal of belt-driven assemblies 3. Installation of direct-driven fans, integration of VFD and automation controls, testing and commissioning 4. Performance validation for energy savings.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 2,28,325 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 91,330 kWh/year |
| Annual saving Rs/year | ₹12,30,215 |
| Investment Rs | ₹27,82,546 |
| Payback, months | 27.14 months |
| Payback, years | 2.26 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| AHU | ₹10,60,217 |
| AHU | ₹2,37,329 |
| AHU | ₹14,85,000 |

### M&V Plan

- Measure motor kW, airflow, static pressure and operating hours.

- Compare before and after fan or blower energy use.

- Verify ventilation, comfort or process requirement is maintained.

### Benefits

- Reduces energy use in the AHU Plug Fan System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 10 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 11: Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 11 |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| System | Air Washer Plug Fan System |
| Equipment covered | Air Washer |
| Baseline kWh/year | 1,59,074 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 63,630 kWh/year |
| Annual saving Rs/year | ₹8,57,091 |
| Investment Rs | ₹23,13,031 |
| Payback, months | 32.38 months |
| Payback, years | 2.7 years |

### Existing Condition

Air Washer. YEARLY AIR -WASHER KWH CONSUMPTION 1. Air Washer 01 Terrace - OFF 2. Air Washer 02 Terrace (3,700cfm@60mmwg) - 5,310 kWh/year 3. Air Washer 03 Terrace (14,500cfm@60mmwg) - 17,248 kWh/year 4. Air Washer 04 Terrace (14,500cfm@60mmwg) - 25,297 kWh/year 5. Air Washer 05 Terrace - OFF 6. Air Washer 06 Terrace (14,500cfm@60mmwg) - 31,532 kWh/year 7. Air Washer 07 Terrace (22,000cfm@60mmwg) - 10,527 kWh/year 8. Air Washer 08 Terrace (22,000cfm@60mmwg) - 20,012 kWh/year 9. Air Washer 09 Terrace (22,200cfm@60mmwg) - 28,696 kWh/year 10. Air Washer 10 Terrace (26,000cfm@60mmwg) - 20,452 kWh/year

### Problem / Gap

Belt driven fan, IE2 efficiency motor

### Proposed Project

Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation. Upgrading to direct-driven aerofoil plug fans with IE5 motors eliminates belt losses and enhances airflow efficiency. The system benefits from reduced power consumption, lower maintenance requirements, and improved operational stability. Automation enables demand-based control, resulting in optimized energy utilization and improved environmental control.

### Project Activities

- Selection and sizing of suitable plug fans and IE5 motors 2. Removal of belt-driven assemblies 3. Installation of direct-driven fans, integration of VFD and automation controls, testing and commissioning 4. Performance validation for energy savings.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 1,59,074 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 63,630 kWh/year |
| Annual saving Rs/year | ₹8,57,091 |
| Investment Rs | ₹23,13,031 |
| Payback, months | 32.38 months |
| Payback, years | 2.7 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| Air Washer | ₹1,36,160 |
| Air Washer | ₹8,16,071 |
| Air Washer | ₹13,60,800 |

### M&V Plan

- Measure motor kW, airflow, static pressure and operating hours.

- Compare before and after fan or blower energy use.

- Verify ventilation, comfort or process requirement is maintained.

### Benefits

- Reduces energy use in the Air Washer Plug Fan System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 11 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 12: Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 12 |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| System | Heat Recovery Wheel / Ventilation Fan System |
| Equipment covered | HRW (Heat Recovery Wheel) |
| Baseline kWh/year | 4,47,145 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 1,78,858 kWh/year |
| Annual saving Rs/year | ₹24,09,217 |
| Investment Rs | ₹36,41,850 |
| Payback, months | 18.14 months |
| Payback, years | 1.51 years |

### Existing Condition

HRW (Heat Recovery Wheel). YEARLY HRW KWH CONSUMPTION 1.1. Heat Recovery Wheel Fresh Air 1 (26,000cfm@50mmwg) - 60,468 kWh/Year 1.1. Heat Recovery Wheel Exhaust Air 1 (20,800cfm@50mmwg) - 36,290 kWh/Year 2.1. Heat Recovery Wheel Fresh Air 2 (26,000cfm@50mmwg) - 38,719 kWh/Year 2.2. Heat Recovery Wheel Exhaust Air 2 - OFF 3.1. Heat Recovery Wheel Fresh Air 3 (26,000cfm@50mmwg) - 48,779 kWh/Year 3.2. Heat Recovery Wheel Exhaust Air 3 (26,000cfm@50mmwg) - 47,479 kWh/Year 4.1. Heat Recovery Wheel Fresh Air 4 (24,000cfm@50mmwg) - 31,155 kWh/Year 4.2. Heat Recovery Wheel Exhaust Air 4 - OFF 5.1. Heat Recovery Wheel Fresh Air 5 (21,500cfm@50mmwg) - 36,494 kWh/Year 5.2. Heat Recovery Wheel Exhaust Air 5 - OFF 6.1. Heat Recovery Wheel Fresh Air 6 (24,000cfm@50mmwg) - 27,975 kWh/Year 6.2. Heat Recovery Wheel Exhaust Air 6 - OFF 7.1. Heat Recovery Wheel Fresh Air 7 (24,000cfm@50mmwg) - 46,246 kWh/Year 7.2. Heat Recovery Wheel Exhaust Air 7 - OFF 8.1. Heat Recovery Wheel Fresh Air 8 (17,000cfm@50mmwg) - 38,448 kWh/Year 8.2. Heat Recovery Wheel Exhaust Air 8 - OFF 9.1. Heat Recovery Wheel Fresh Air 9 (17,000cfm@50mmwg) - 35,093 kWh/Year 9.2. Heat Recovery Wheel Exhaust Air 9 - OFF

### Problem / Gap

Belt driven fan, IE2 efficiency motor

### Proposed Project

Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation. Upgrading to direct-driven aerofoil plug fans with IE5 motors eliminates belt losses and enhances airflow efficiency. The system benefits from reduced power consumption, lower maintenance requirements, and improved operational stability. Automation enables demand-based control, resulting in optimized energy utilization and improved environmental control.

### Project Activities

- Selection and sizing of suitable plug fans and IE5 motors 2. Removal of belt-driven assemblies 3. Installation of direct-driven fans, integration of VFD and automation controls, testing and commissioning 4. Performance validation for energy savings.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 4,47,145 kWh/year |
| Saving % | 40% |
| Energy saving kWh/year | 1,78,858 kWh/year |
| Annual saving Rs/year | ₹24,09,217 |
| Investment Rs | ₹36,41,850 |
| Payback, months | 18.14 months |
| Payback, years | 1.51 years |

### Costing Backup

| Item | Total Cost |
| --- | --- |
| HRW | ₹12,32,375 |
| HRW | ₹2,71,755 |
| HRW | ₹13,50,000 |
| HRW | ₹7,87,721 |

### M&V Plan

- Measure motor kW, airflow, static pressure and operating hours.

- Compare before and after fan or blower energy use.

- Verify ventilation, comfort or process requirement is maintained.

### Benefits

- Reduces energy use in the Heat Recovery Wheel / Ventilation Fan System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 12 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

## ECM 13: Scrubber motor retrofit with high efficiency motor with VFD and DCV automation

| Particular | Value |
| --- | --- |
| ECM No. | ECM 13 |
| Project title | Scrubber motor retrofit with high efficiency motor with VFD and DCV automation |
| System | Scrubber Ventilation Motor System |
| Equipment covered | Srubber Unit |
| Baseline kWh/year | 3,29,766 kWh/year |
| Saving % | 25% |
| Energy saving kWh/year | 82,442 kWh/year |
| Annual saving Rs/year | ₹11,10,487 |
| Investment Rs | ₹22,00,000 |
| Payback, months | 23.77 months |
| Payback, years | 1.98 years |

### Existing Condition

Srubber Unit. YEARLY SCRUBBER KWH CONSUMPTION 1. Scrubber 01 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM)- 40686 kWh/Year 2. Scrubber 02 Terrace (4,600cfm@70mmwg, 3.7kW, 1500 RPM) - 11,826 kWh/Year 3. Scrubber 03 Terrace (17,800cfm@70mmwg, 11kW, 1500 RPM) - 38,982 kWh/Year 4. Scrubber 04 Terrace (17,800cfm@70mmwg, 11kW, 1500 RPM) - 26,017 kWh/Year 5. Scrubber 05 Terrace (17,800cfm@60mmwg, 7.5kW, 1500 RPM) - 21,854 kWh/Year 6. Scrubber 06 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 39,902 kWh/Year 7. Scrubber 07 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 37,935 kWh/Year 8. Scrubber 08 Terrace (17,800cfm@60mmwg, 7.5kW, 1500 RPM) - 39,823 kWh/Year 9. Scrubber 09 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 49,363 kWh/Year 10. Scrubber 10 Terrace (24,700cfm@50mmwg, 7.5kW, 1500 RPM) - 23,378 kWh/Year

### Problem / Gap

IE2 efficincy class motor and no automation

### Proposed Project

Scrubber motor retrofit with high efficiency motor with VFD and DCV automation. Upgrading scrubber motors to high-efficiency IE5 motors with VFD and DCV (Demand Control Ventilation) improves energy efficiency by matching motor speed with process requirements. This reduces unnecessary power consumption, enhances process control, and extends equipment life while lowering maintenance costs.

### Project Activities

- Analysis of existing motor performance and load profile, selection of IE5 high-efficiency motors and VFD systems, installation and integration with DCV controls, system tuning for optimal performance, and validation of energy savings through monitoring and data analysis.

### Energy Saving Calculation

| Particular | Value |
| --- | --- |
| Baseline kWh/year | 3,29,766 kWh/year |
| Saving % | 25% |
| Energy saving kWh/year | 82,442 kWh/year |
| Annual saving Rs/year | ₹11,10,487 |
| Investment Rs | ₹22,00,000 |
| Payback, months | 23.77 months |
| Payback, years | 1.98 years |

### M&V Plan

- Measure motor kW, airflow, static pressure and operating hours.

- Compare before and after fan or blower energy use.

- Verify ventilation, comfort or process requirement is maintained.

### Benefits

- Reduces energy use in the Scrubber Ventilation Motor System system.

- Lowers annual electricity cost based on the extracted billing tariff.

- Supports more stable and controllable operation.

### Conclusion

- ECM 13 is supported by the uploaded ECM source data.

- Financial metrics are taken directly from extracted source values.

- Proceed with implementation after the remaining Annexure B inputs are field-verified, where applicable.

# 7. Measurement & Verification Plan

| ECM No. | Project Title | M&V Plan |
| --- | --- | --- |
| ECM 1 | Contract Demand Optimization | Compare monthly recorded demand and billed demand before and after contract demand revision.; Verify demand charge reduction from utility bills.; Confirm no demand penalty occurs after revision. |
| ECM 2 | Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement | Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.; Compare kW/TR before and after implementation.; Normalize comparison for cooling load and operating hours. |
| ECM 3 | Cooling tower motor retrofit with high efficiency PMS motor wirh VFD and automation | Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.; Compare kW/TR before and after implementation.; Normalize comparison for cooling load and operating hours. |
| ECM 4 | Increase the set point of chiller as the return water is 9.4 deg C and delta t is 2.9 deg c (chilled water supply is 6.5 deg c) | Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.; Compare kW/TR before and after implementation.; Normalize comparison for cooling load and operating hours. |
| ECM 5 | Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand | Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.; Compare kW/TR before and after implementation.; Normalize comparison for cooling load and operating hours. |
| ECM 18 | Energy Saving in Chiller by improving operational practices | Record chiller kW, CHWS/CHWR temperature, condenser water temperature and cooling tower operation.; Compare kW/TR before and after implementation.; Normalize comparison for cooling load and operating hours. |
| ECM 6 | Condenser pump motor refrofit with high efficiency motor (IE4/IE5) with VFD and delta t & delta p automation | Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.; Compare before/after kW under similar load.; Verify stable flow or pressure after control changes. |
| ECM 7 | Primary pump motor refrofit with high efficiency motor IE5 with VFD and delta t & delta p automation | Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.; Compare before/after kW under similar load.; Verify stable flow or pressure after control changes. |
| ECM 8 | Secondary pump motor refrofit with high efficiency motor IE5 with existing VFD and delta t & delta p automation | Measure pump kW, flow/head or differential pressure, VFD frequency and operating hours.; Compare before/after kW under similar load.; Verify stable flow or pressure after control changes. |
| ECM 9 | Existing IE2 efficiency class retrofit with high efficieny motor (IE5) and cogged belt | Measure motor kW, airflow, static pressure and operating hours.; Compare before and after fan or blower energy use.; Verify ventilation, comfort or process requirement is maintained. |
| ECM 10 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Measure motor kW, airflow, static pressure and operating hours.; Compare before and after fan or blower energy use.; Verify ventilation, comfort or process requirement is maintained. |
| ECM 11 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Measure motor kW, airflow, static pressure and operating hours.; Compare before and after fan or blower energy use.; Verify ventilation, comfort or process requirement is maintained. |
| ECM 12 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Measure motor kW, airflow, static pressure and operating hours.; Compare before and after fan or blower energy use.; Verify ventilation, comfort or process requirement is maintained. |
| ECM 13 | Scrubber motor retrofit with high efficiency motor with VFD and DCV automation | Measure motor kW, airflow, static pressure and operating hours.; Compare before and after fan or blower energy use.; Verify ventilation, comfort or process requirement is maintained. |

# 8. Annexure A: Extracted Data Summary

| Particular | Value |
| --- | --- |
| Client name | M/S VR DAKSHIN PRIVATE LIMITED |
| Service number | 019094061918 |
| Monthly bills extracted | 12 |
| ECMs extracted | 14 |
| Connected load systems | 20 |
| PDF files detected | 13 |
| PDF files parsed | 13 |

## PDF Parse Status

| Particular | Value |
| --- | --- |
| Files detected | 13 |
| Files parsed | 13 |
| Files failed | 0 |
| Warnings |  |

# 9. Annexure B: Missing Inputs Required

| Section | Missing Input | Why Required | Suggested Source | Criticality |
| --- | --- | --- | --- | --- |
| Benchmarking | Built-up area | Required for SEC benchmark. | Building drawing / client data | Medium |
| Benchmarking | Conditioned area | Required for HVAC benchmark. | HVAC layout / BMS | Medium |
| Detailed ECM Sheets | Chiller TR rating | Required for kW/TR validation. | Chiller nameplate / BMS | High |
| Detailed ECM Sheets | Pump head and flow | Required for pump ECM validation. | Pump datasheet / site measurement | High |
| Detailed ECM Sheets | AHU CFM and static pressure confirmation | Required for plug fan ECM validation. | AHU schedule / site measurement | High |
| Reporting | CO2 emission factor | Required for carbon calculation. | Client-approved factor | Low |
| Detailed ECM Sheets | ECM 2 existing condition details | Required to expand the existing-condition narrative. | ECM sheet / site verification | Medium |
| Detailed ECM Sheets | ECM 4 problem statement | Required to explain the basis of the ECM recommendation. | ECM sheet / site verification | Medium |
| Detailed ECM Sheets | ECM 18 existing condition details | Required to expand the existing-condition narrative. | ECM sheet / site verification | Medium |
| Detailed ECM Sheets | ECM 6 existing condition details | Required to expand the existing-condition narrative. | ECM sheet / site verification | Medium |
| Detailed ECM Sheets | ECM 7 existing condition details | Required to expand the existing-condition narrative. | ECM sheet / site verification | Medium |
| Detailed ECM Sheets | ECM 8 existing condition details | Required to expand the existing-condition narrative. | ECM sheet / site verification | Medium |
| ECM Costing | Costing backup not found for ECM 13. | Required to support BOQ and implementation costing backup. | Costing / Blower Costing sheet | High |