SEE-Tech Solutions

Industrial Energy Audit Report Format

Detailed Energy Audit Report

Purpose: To identify implementable energy-saving projects with clear investment, savings, payback and execution roadmap.

| Prepared For | To be confirmed |
| --- | --- |
| Building Type | To be confirmed |
| Location | To be confirmed |
| Audit Period | To be confirmed |
| Report Date | 25 June 2026 |
| Prepared By | SEE-Tech Solutions |
| Document Version | Rev. 0 |

# Table of Contents

Chapter 1. Executive Summary

1.1 Purpose of the Energy Audit

1.2 Key Objectives

1.3 Scope of Assessment

1.4 Expected Outcomes

1.5 Strategic Importance

1.6 Key Findings

1.7 Financial Highlights

1.8 Energy Saving Potential

1.9 Recommended Implementation Approach

Chapter 2. Plant / Building Details and Energy Profile

2.1 About the Facility

2.2 Production Facility Operation Details

2.3 Utility and Energy Sources

2.4 Electrical Supply Details

2.5 Electricity Consumption and Billing Summary

2.6 Specific Energy Consumption Benchmark

2.7 Major Energy Consuming Systems

2.8 HVAC System Details

2.9 Lighting System Details

2.10 Pumps and Motors

2.11 Building Automation and Controls

2.12 Summary of Audit Observations

Chapter 3. Energy Saving Projects

3.1 ECM 1 – Contract Demand Optimization

3.2 ECM 2 – Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement

3.3 ECM 3 – Cooling tower motor retrofit with high efficiency PMS motor with VFD and automation

3.4 ECM 4 – Increase the set point of chiller as the return water is 9.4 °C and ΔT is 2.9 °C (chilled water supply is 6.5 °C)

3.5 ECM 5 – Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand

3.6 ECM 6 – Condenser pump motor retrofit with high efficiency motor (IE4/IE5) with VFD and ΔT & ΔP automation

3.7 ECM 7 – Primary pump motor retrofit with high efficiency motor IE5 with VFD and ΔT & ΔP automation

3.8 ECM 8 – Secondary pump motor retrofit with high efficiency motor IE5 with existing VFD and ΔT & ΔP automation

3.9 ECM 9 – Existing IE2 efficiency class retrofit with high efficiency motor (IE5) and cogged belt

3.10 ECM 10 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

3.11 ECM 11 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

3.12 ECM 12 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

3.13 ECM 13 – Scrubber motor retrofit with high efficiency motor with VFD and DCV automation

3.14 ECM 18 – Energy Saving in Chiller by improving operational practices

Chapter 4. Annexures

# Chapter 1: Executive Summary

## 1.1 Purpose of the Energy Audit

• The purpose of this energy audit is to evaluate the electrical energy consumption pattern of the facility, identify major energy-consuming systems, and develop technically and financially viable energy conservation measures. The audit focuses on reducing energy cost, improving system efficiency, and supporting structured implementation of ECMs.

## 1.2 Key Objectives

• Analyse monthly electricity consumption, demand, power factor and tariff impact.

• Identify major energy-consuming systems and quantify their contribution to annual consumption.

• Evaluate energy conservation measures with estimated savings, investment and payback.

• Provide a prioritized implementation roadmap for operational and capital improvement projects.

## 1.3 Scope of Assessment

• Comprehensive review of historical energy consumption patterns and utility billing data.

• Detailed performance evaluation of major energy-consuming systems including HVAC, compressed air, pumping, and production machinery.

• Assessment of existing control logic, operating practices, and maintenance procedures impacting energy efficiency.

## 1.4 Expected Outcomes

• A prioritized portfolio of energy conservation measures (ECMs) categorized by technical feasibility and financial return.

• Clear recommendations for immediate operational improvements requiring minimal capital investment.

• Strategic guidance for long-term capital planning related to major equipment replacements and system retrofits.

## 1.5 Strategic Importance

• Enhances operational resilience by reducing exposure to energy price volatility and supply constraints.

• Supports corporate sustainability goals through quantifiable reductions in carbon emissions and environmental impact.

• Improves overall facility competitiveness by lowering production costs and optimizing resource utilization.

## 1.6 Key Findings

• The identified ECM portfolio covers multiple functional systems, allowing management to sequence implementation across operational improvements, control upgrades, and equipment-efficiency measures instead of treating all projects as a single package.

• Measures linked to operating control, load matching, and reduction of avoidable system losses are generally suitable early implementation candidates because they strengthen performance discipline while preparing the site team for larger retrofit actions.

• Projects associated with major utility systems and continuously operating process support equipment warrant close management attention because sustained operating hours make these systems important contributors to the overall energy-improvement roadmap.

## 1.7 Financial Highlights

• The proposed energy conservation measures offer a highly attractive financial return, driven by significant reductions in annual operating costs.

• A balanced mix of low-cost operational improvements and high-return capital projects provides a robust investment portfolio for management consideration.

| Particular | Value |
| --- | --- |
| Total annual electricity consumption |  |
| Annual electricity cost |  |
| Average electricity tariff considered |  |
| Number of projects identified | 14 |
| Total energy saving potential | 29,35,731 |
| Total annual cost saving potential | ₹3,95,44,302 |
| Total estimated investment | ₹2,70,55,427 |
| Simple payback period | 0.68 |
| CO2 reduction potential | [Calculation pending due to missing emission factor] |

## 1.8 Energy Saving Potential

• Substantial energy savings can be achieved through a combination of enhanced system controls, elimination of avoidable losses, and targeted equipment upgrades.

• The projected energy reductions are grounded in verified baseline data and conservative engineering calculations to ensure reliable and achievable outcomes.

| ECM No. | Energy Saving Project | System | Investment | Annual Saving | Energy Saving kWh/y |
| --- | --- | --- | --- | --- | --- |
| ECM 1 | Contract Demand Optimization | Electrical Billing / Demand Management | ₹2,00,000 | ₹1,05,06,240 | 7,79,973 |
| ECM 2 | Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement | Cooling Tower / Chiller Condenser System | ₹24,00,000 | ₹36,69,783 | 2,72,441 |
| ECM 3 | Cooling tower motor retrofit with high efficiency PMS motor with VFD and automation | Cooling Tower Fan System | ₹17,50,000 | ₹5,17,523 | 38,420 |
| ECM 4 | Increase the set point of chiller as the return water is 9.4 °C and ΔT is 2.9 °C (chilled water supply is 6.5 °C) | Chiller Plant Controls / CHW Set Point | ₹10,00,000 | ₹29,35,826 | 2,17,953 |
| ECM 5 | Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand | Chiller Plant Automation and Sequencing | ₹60,00,000 | ₹1,15,38,605 | 8,56,615 |
| ECM 6 | Condenser pump motor retrofit with high efficiency motor (IE4/IE5) with VFD and ΔT & ΔP automation | Condenser Water Pumping System | ₹15,93,000 | ₹8,13,133 | 60,366 |
| ECM 7 | Primary pump motor retrofit with high efficiency motor IE5 with VFD and ΔT & ΔP automation | Primary CHW Pumping System | ₹13,50,000 | ₹6,46,523 | 47,997 |
| ECM 8 | Secondary pump motor retrofit with high efficiency motor IE5 with existing VFD and ΔT & ΔP automation | Secondary CHW Pumping System | ₹14,25,000 | ₹6,16,181 | 45,745 |
| ECM 9 | Existing IE2 efficiency class retrofit with high efficiency motor (IE5) and cogged belt | STP Blower / Motor Drive System | ₹4,00,000 | ₹2,35,994 | 17,520 |
| ECM 10 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | AHU Plug Fan System | ₹27,82,546 | ₹12,30,215 | 91,330 |
| ECM 11 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Air Washer Plug Fan System | ₹23,13,031 | ₹8,57,091 | 63,630 |
| ECM 12 | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation | Heat Recovery Wheel / Ventilation Fan System | ₹36,41,850 | ₹24,09,217 | 1,78,858 |
| ECM 13 | Scrubber motor retrofit with high efficiency motor with VFD and DCV automation | Scrubber Ventilation Motor System | ₹22,00,000 | ₹11,10,487 | 82,442 |
| ECM 18 | Energy Saving in Chiller by improving operational practices | Chiller Operational Practice Improvement | ₹0 | ₹24,57,483 | 1,82,441 |

## 1.9 Recommended Implementation Approach

• The audit has identified a portfolio of energy conservation measures with measurable energy and cost saving potential. The recommended way forward is to validate pending site inputs, prioritize short-payback measures, finalize implementation responsibilities, and monitor savings through a structured M&V plan.

### 1.9.1 Recommended Implementation Priority

| Priority Level | ECM Numbers | Reason for Priority | Investment | Annual Saving | Payback | Implementation Note |
| --- | --- | --- | --- | --- | --- | --- |
| Medium Priority | ECM 1 | Moderate payback 1.5 - 3 years | ₹2,00,000 | ₹1,05,06,240 | 2 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 18 | Moderate payback 1.5 - 3 years | ₹0 | ₹24,57,483 | 0 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 2 | Longer payback or high capex | ₹24,00,000 | ₹36,69,783 | 65 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 3 | Longer payback or high capex | ₹17,50,000 | ₹5,17,523 | 38 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 4 | Longer payback or high capex | ₹10,00,000 | ₹29,35,826 | 34 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 5 | Longer payback or high capex | ₹60,00,000 | ₹1,15,38,605 | 52 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 6 | Longer payback or high capex | ₹15,93,000 | ₹8,13,133 | 96 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 7 | Longer payback or high capex | ₹13,50,000 | ₹6,46,523 | 9 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 8 | Longer payback or high capex | ₹14,25,000 | ₹6,16,181 | 31 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 9 | Longer payback or high capex | ₹4,00,000 | ₹2,35,994 | 69 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 10 | Longer payback or high capex | ₹27,82,546 | ₹12,30,215 | 26 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 11 | Longer payback or high capex | ₹23,13,031 | ₹8,57,091 | 70 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 12 | Longer payback or high capex | ₹36,41,850 | ₹24,09,217 | 51 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 13 | Longer payback or high capex | ₹22,00,000 | ₹11,10,487 | 98 | Implementation complexity to be finalized after site verification. |

### 1.9.2 Action Plan

| Step | Action |
| --- | --- |
| 1 | Site verification |
| 2 | Vendor quotation / detailed engineering |
| 3 | Implementation scheduling |
| 4 | M&V baseline confirmation |
| 5 | Execution |
| 6 | Post-implementation verification |

# Chapter 2: Plant / Building Details and Energy Profile

## 2.1 General Information

| Name of facility | M/S VR DAKSHIN PRIVATE LIMITED |
| --- | --- |
| Address | NO .44,PILLAYAR KOIL STREETJAWAHARLAL NEHRU SALAI,THIRUMANGALABEHIND VEE CARE HOSPITAL CHENNAI - 600 040 |
| Type of building | Commercial Mall / Retail Building |
| Year of construction | To be updated |
| Total built-up area | To be updated |
| Conditioned area | To be updated |
| Number of floors | To be updated |
| Occupancy type | To be updated |
| Average occupancy | To be updated |
| Operating days and hours | To be updated |
| Facility contact person | To be updated |
| Audit date | Audit Period |
| SEE-Tech audit team | SEE-Tech Solutions |

## 2.2 Production Facility Operation Details

| Area / Function | Operating Hours | Remarks |
| --- | --- | --- |
| Production areas | To be updated | To be updated |
| Utility block | To be updated | To be updated |
| Chiller plant | To be updated | To be updated |
| Compressor room | To be updated | To be updated |
| Dryer section | To be updated | To be updated |
| Injection/stretch blow molding machines | To be updated | To be updated |
| AHU/clean room area | To be updated | To be updated |
| Electrical room/APFC | To be updated | To be updated |
| Maintenance/utilities | To be updated | To be updated |

## 2.3 Utility and Energy Sources

| Energy Source | Use | Annual Consumption | Annual Cost ₹ |
| --- | --- | --- | --- |
| Grid electricity | Facility operations | 2,17,82,502 kWh | ₹28,65,88,021 |

## 2.4 Electrical Supply Details

| Supply voltage | 33 kV |
| --- | --- |
| Consumer number | 019094061918 |
| Tariff category | HT III / HT III |
| Contract demand / sanctioned load | 7,000 kVA |
| Connected load | To be updated |
| Transformer capacity | To be updated |
| DG capacity | To be updated |
| APFC panel capacity | To be updated |
| Average power factor | To be updated |
| Billing type | To be updated |
| Average electricity tariff | ₹13/kWh |

## 2.5 Electricity Consumption and Billing Summary

| Month | kWh | kVAh | Maximum Demand kVA | PF | Bill Amount ₹ | Specific Consumption |
| --- | --- | --- | --- | --- | --- | --- |
| Feb 2025 | 16,30,305 kWh | 16,35,278 kVAh | 4,200 kVA | 1 | ₹2,14,55,083 | To be updated |
| Mar 2025 | 18,34,463 kWh | Verify from bill PDF | 4,425 kVA | Verify from bill PDF | ₹2,31,10,905 | To be updated |
| Apr 2025 | 18,62,685 kWh | 18,93,810 kVAh | 4,755 kVA | 98 | ₹2,45,41,621 | To be updated |
| May 2025 | 19,40,333 kWh | 19,78,665 kVAh | 4,718 kVA | 98 | ₹2,47,66,581 | To be updated |
| Jun 2025 | 18,12,623 kWh | 18,50,250 kVAh | 4,628 kVA | 98 | ₹2,34,31,316 | To be updated |
| Jul 2025 | 18,88,688 kWh | 19,31,760 kVAh | 4,650 kVA | 98 | ₹2,50,20,074 | To be updated |
| Aug 2025 | 19,40,888 kWh | 19,83,443 kVAh | 4,695 kVA | 98 | ₹2,55,98,144 | To be updated |
| Sep 2025 | 18,14,865 kWh | 18,51,900 kVAh | 4,710 kVA | 98 | ₹2,42,15,435 | To be updated |
| Oct 2025 | 18,82,658 kWh | 19,17,615 kVAh | 4,553 kVA | 98 | ₹2,49,40,585 | To be updated |
| Nov 2025 | 17,53,433 kWh | 17,83,290 kVAh | 4,523 kVA | 98 | ₹2,34,94,143 | To be updated |
| Dec 2025 | 17,27,423 kWh | 17,55,540 kVAh | 4,425 kVA | 98 | ₹2,31,97,403 | To be updated |
| Jan 2026 | 16,94,138 kWh | 17,27,108 kVAh | 4,223 kVA | 98 | ₹2,28,16,731 | To be updated |

## 2.6 Specific Energy Consumption Benchmark

| Building Type | Recommended Benchmark |
| --- | --- |
| Production areas | kWh/kg product or kWh/machine-hour |
| Utility block | kWh/ton utility output or kWh/day |
| Compressed air system | kW/CFM or kWh/Nm3 |
| Chiller plant | kW/TR and kWh/TRh |
| Dryer section | kWh/kg moisture removed |
| Clean room / AHU area | kWh/sq.ft/year or kWh/air-change |

| Annual electricity consumption | To be updated |
| --- | --- |
| Built-up area | To be updated |
| Conditioned area | To be updated |
| Annual occupancy / room nights / bed days | To be updated |
| Specific energy consumption | To be updated |
| Reference / target benchmark | To be updated |
| Improvement potential | To be updated |

## 2.7 Major Energy-Consuming Systems

| System | Major Equipment | Estimated Share of Energy Consumption | Remarks |
| --- | --- | --- | --- |
| Chiller | Chiller | 74% | Counted from 3 equipment rows |
| Condenser Pump | Condenser Pump | 04% | Counted from 3 equipment rows |
| Secondary CHW Pump | Secondary CHW Pump | 64% | Counted from 4 equipment rows |
| Primary CHW Pump | Primary CHW Pump | 57% | Counted from 4 equipment rows |
| Heat Recovery Wheel fresh air | Heat Recovery Wheel fresh air | 27% | Counted from 9 equipment rows |
| Scrubber | Scrubber | 62% | Counted from 10 equipment rows |
| Escalator | Escalator | 77% | Counted from 24 equipment rows |
| AHU | AHU | 5% | Counted from 12 equipment rows |
| Cooling Tower | Cooling Tower | 27% | Counted from 4 equipment rows |
| Air Washer | Air Washer | 74% | Counted from 10 equipment rows |
| CSU | CSU | 65% | Counted from 22 equipment rows |
| Softener Pump | Softener Pump | 33% | Counted from 1 equipment row |
| STP Blower | STP Blower | 33% | Counted from 1 equipment row |
| Heat Recovery Wheel exhaust | Heat Recovery Wheel exhaust | 75% | Counted from 9 equipment rows |
| Office Outdoor | Office Outdoor | 63% | Counted from 2 equipment rows |
| Domestic Pump | Domestic Pump | 75% | Counted from 2 equipment rows |
| Lift | Lift | 67% | Counted from 10 equipment rows |
| Flush Pump | Flush Pump | 33% | Counted from 2 equipment rows |
| FCU | FCU | 17% | Counted from 10 equipment rows |
| Irrigation Pump | Irrigation Pump | 4% | Counted from 1 equipment row |

## 2.8 HVAC System Details

| Equipment | Capacity | Quantity | Connected Load | Control System | Remarks |
| --- | --- | --- | --- | --- | --- |
| Chiller | To be updated | 3 | 1,052.96 kW | To be updated | Counted from 3 equipment rows |
| Heat Recovery Wheel fresh air | To be updated | 9 | 22 kW | To be updated | Counted from 9 equipment rows |
| AHU | To be updated | 12 | 13 kW | To be updated | Counted from 12 equipment rows |
| Cooling Tower | To be updated | 4 | 59 kW | To be updated | Counted from 4 equipment rows |
| Air Washer | To be updated | 10 | 32 kW | To be updated | Counted from 10 equipment rows |
| Heat Recovery Wheel exhaust | To be updated | 9 | 09 kW | To be updated | Counted from 9 equipment rows |

The utility cooling and ventilation systems are major energy-consuming assets in an industrial facility. During the audit, operating hours, thermal load variation, chilled-water temperature control, pump and fan operation, clean-room or process ventilation requirements, and maintenance condition should be reviewed. Key opportunities may relate to variable speed operation, chiller efficiency, flow optimization, cooling tower performance, AHU scheduling, and set-point discipline.

## 2.9 Lighting System Details

| Area | Existing Fixture | Wattage | Quantity | Operating Hours | Control Type |
| --- | --- | --- | --- | --- | --- |
| Production hall | To be updated | To be updated | To be updated | To be updated | To be updated |
| Utility block | To be updated | To be updated | To be updated | To be updated | To be updated |
| Compressor room | To be updated | To be updated | To be updated | To be updated | To be updated |
| Dryer section | To be updated | To be updated | To be updated | To be updated | To be updated |
| Electrical room | To be updated | To be updated | To be updated | To be updated | To be updated |
| Warehouse / dispatch | To be updated | To be updated | To be updated | To be updated | To be updated |

Lighting energy consumption in industrial facilities can be reduced through LED retrofits, lux optimization, zoning, and occupancy or schedule-based controls. Production aisles, utility rooms, warehouses, and support areas should be reviewed for over-lighting, legacy fixtures, and control opportunities.

## 2.10 Pumps and Motors

| Pump / Motor | Application | Rating kW | Quantity | Operating Hours | Control Method | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Condenser Pump | To be updated | 01 kW | 3 | To be updated | To be updated | Counted from 3 equipment rows |
| Secondary CHW Pump | To be updated | 38 kW | 4 | To be updated | To be updated | Counted from 4 equipment rows |
| Primary CHW Pump | To be updated | 77 kW | 4 | To be updated | To be updated | Counted from 4 equipment rows |
| Scrubber | To be updated | 29 kW | 10 | To be updated | To be updated | Counted from 10 equipment rows |
| Softener Pump | To be updated | 81 kW | 1 | To be updated | To be updated | Counted from 1 equipment row |
| STP Blower | To be updated | 20 kW | 1 | To be updated | To be updated | Counted from 1 equipment row |
| Domestic Pump | To be updated | 96 kW | 2 | To be updated | To be updated | Counted from 2 equipment rows |
| Flush Pump | To be updated | 86 kW | 2 | To be updated | To be updated | Counted from 2 equipment rows |
| Irrigation Pump | To be updated | 3 kW | 1 | To be updated | To be updated | Counted from 1 equipment row |

## 2.11 Building Automation and Controls

| System | Existing Control | Observation | Saving Opportunity |
| --- | --- | --- | --- |
| HVAC scheduling | To be updated | To be updated | To be updated |
| AHU control | To be updated | To be updated | To be updated |
| Pump control | To be updated | To be updated | To be updated |
| Lighting control | To be updated | To be updated | To be updated |
| Parking ventilation | To be updated | To be updated | To be updated |
| Temperature set point | To be updated | To be updated | To be updated |
| Energy monitoring | To be updated | To be updated | To be updated |

## 2.12 Summary of Audit Observations

| Sr. No. | Observation | Impact | Recommended Project |
| --- | --- | --- | --- |
| 1 | To be updated | High energy consumption | To be updated |
| 2 | To be updated | Higher demand / kVAh billing | To be updated |
| 3 | To be updated | Excess operating hours | To be updated |
| 4 | To be updated | Inefficient equipment | To be updated |
| 5 | To be updated | Poor control / manual operation | To be updated |

# Chapter 3: Energy Saving Projects

This chapter presents the identified energy conservation measures in the sequence extracted from the uploaded ECM sheet.

3.1 ECM 1 – Contract Demand Optimization

### 3.1.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Contract Demand Optimization |
| Project number | ECM 1 |
| System | Electrical Billing / Demand Management |
| Location | To be updated |
| Equipment covered | Meter |
| Existing operating condition | The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization. |
| Proposed intervention | The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization. |
| Expected energy saving | 7,79,973 kWh/year |
| Expected annual cost saving | ₹1,05,06,240 |
| Estimated investment | ₹2,00,000 |
| Simple payback period | 2 years |
| Implementation duration | To be updated |
| Implementation priority | I |

### 3.1.2 Existing System Description

• Monthly Recorded Maximum Demand (kVA) 1. Feb 2025 – 4200 kVA 2. Mar 2025 – 4425 kVA 3. Apr 2025 – 4755 kVA (highest) 4. May 2025 – 4718 kVA 5. Jun 2025 – 4628 kVA 6. Jul 2025 – 4650 kVA 7. Aug 2025 – 4695 kVA 8. Sep 2025 – 4710 kVA 9. Oct 2025 – 4553 kVA 10. Nov 2025 – 4523 kVA 11. Dec 2025 – 4425 kVA 12. Jan 2026 – 4223 kVA Average: 4542 kVA

### 3.1.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.1.4 Problem / Gap Identified

• Since the highest MD recorded in April 2025 is 4755 kVA, there is a strong opportunity to optimize the contract demand and avoid unnecessary demand charges from the utility

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.1.5 Proposed Project

• Contract Demand Optimization

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.1.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.1.7 Rationale for Energy Saving

• The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.1.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 7,79,973 |
| Annual cost saving | ₹/year | ₹1,05,06,240 |
| Estimated investment | ₹ | ₹2,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.1.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | [Calculation pending] |
| 2 | Energy saving | 7,79,973 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,05,06,240 |
| 5 | Estimated investment | ₹2,00,000 |
| 6 | Payback period (years) | 2 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.1.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.1.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.1.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.1.13 Precautions / Aspects to be Taken Care Of

• The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.1.14 Measurement and Verification Plan

• The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.1.15 Benefits Other Than Energy Saving

• This project optimizes contract demand based on actual Maximum Demand of 4755 kVA recorded in April 2025. The proposed demand is 5400 kVA, providing a safe margin while reducing unnecessary charges. It helps lower electricity costs, control peak demand, and improve efficiency without affecting operations

| Benefit | Description |
| --- | --- |

### 3.1.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.1.17 Case Study / Reference Application

• The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization.

### 3.1.18 Project Conclusion

• The existing system operates under baseline conditions that present measurable opportunities for energy performance optimization.

3.2 ECM 2 – Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement

### 3.2.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement |
| Project number | ECM 2 |
| System | Cooling Tower / Chiller Condenser System |
| Location | To be updated |
| Equipment covered | Cooling Tower 2 & 3 |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 2,72,441 kWh/year |
| Expected annual cost saving | ₹36,69,783 |
| Estimated investment | ₹24,00,000 |
| Simple payback period | 65 years |
| Implementation duration | To be updated |
| Implementation priority | I |

### 3.2.2 Existing System Description

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.2.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 5448824 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.2.4 Problem / Gap Identified

• Cooling tower approach is high, causing the chiller condenser cooling water temperature to reach (WBT + 5°C), which is excessive and resulting in higher chiller power consumption

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.2.5 Proposed Project

• Energy Saving in Chiller by CT Performance Improvement, fan blade angle improvement, damaged fins replacement

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.2.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.2.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.2.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 2,72,441 |
| Annual cost saving | ₹/year | ₹36,69,783 |
| Estimated investment | ₹ | ₹24,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.2.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 5448824 |
| 2 | Energy saving | 2,72,441 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹36,69,783 |
| 5 | Estimated investment | ₹24,00,000 |
| 6 | Payback period (years) | 65 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.2.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.2.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.2.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.2.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.2.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.2.15 Benefits Other Than Energy Saving

• Reducing the cooling tower approach by optimizing fan blade angle and damaged fins replacement improves heat rejection efficiency, which lowers condenser water temperature. This reduces chiller compressor load and power consumption, resulting in energy savings, improved system performance (For every 1°C reduction in condenser water temperature, the chiller compressor power consumption decreases by approximately 2% to 3%).

| Benefit | Description |
| --- | --- |

### 3.2.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.2.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.2.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.3 ECM 3 – Cooling tower motor retrofit with high efficiency PMS motor with VFD and automation

### 3.3.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Cooling tower motor retrofit with high efficiency PMS motor with VFD and automation |
| Project number | ECM 3 |
| System | Cooling Tower Fan System |
| Location | To be updated |
| Equipment covered | Cooling Tower 2 & 3 |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 38,420 kWh/year |
| Expected annual cost saving | ₹5,17,523 |
| Estimated investment | ₹17,50,000 |
| Simple payback period | 38 years |
| Implementation duration | To be updated |
| Implementation priority | III |

### 3.3.2 Existing System Description

• Cooling Tower 2 & 3 Motor Specifictaions (7.5 kW x 4 Nos, 570 RPM, Direct Driven CT Fan, Flange, Frame 180 MV

### 3.3.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 192102 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.3.4 Problem / Gap Identified

• IE2 Efficiency class motor to be changed with IE5 Efficiency class motor

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.3.5 Proposed Project

• Cooling tower motor retrofit with high efficiency PMS motor with VFD and automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.3.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.3.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.3.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 38,420 |
| Annual cost saving | ₹/year | ₹5,17,523 |
| Estimated investment | ₹ | ₹17,50,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.3.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 192102 |
| 2 | Energy saving | 38,420 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹5,17,523 |
| 5 | Estimated investment | ₹17,50,000 |
| 6 | Payback period (years) | 38 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.3.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.3.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.3.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.3.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.3.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.3.15 Benefits Other Than Energy Saving

• Upgrade CT-2 & CT-3 motors from IE2 to high-efficiency IE5 PMS motors with VFD and automation to optimize fan speed as per demand. This reduces energy consumption and improves system efficiency, with expected savings of 15–20%

| Benefit | Description |
| --- | --- |

### 3.3.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.3.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.3.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.4 ECM 4 – Increase the set point of chiller as the return water is 9.4 °C and ΔT is 2.9 °C (chilled water supply is 6.5 °C)

### 3.4.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Increase the set point of chiller as the return water is 9.4 °C and ΔT is 2.9 °C (chilled water supply is 6.5 °C) |
| Project number | ECM 4 |
| System | Chiller Plant Controls / CHW Set Point |
| Location | To be updated |
| Equipment covered | Chiller |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 2,17,953 kWh/year |
| Expected annual cost saving | ₹29,35,826 |
| Estimated investment | ₹10,00,000 |
| Simple payback period | 34 years |
| Implementation duration | To be updated |
| Implementation priority | I |

### 3.4.2 Existing System Description

• Return water = 9.4°C, Supply water = 6.5°C, Delta-T = 2.9°C. Indicates opportunity to optimize set point and improve efficiency

### 3.4.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 5448824 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.4.4 Problem / Gap Identified

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.4.5 Proposed Project

• Increase the set point of chiller as the return water is 9.4 °C and ΔT is 2.9 °C (chilled water supply is 6.5 °C)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.4.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.4.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.4.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 2,17,953 |
| Annual cost saving | ₹/year | ₹29,35,826 |
| Estimated investment | ₹ | ₹10,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.4.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 5448824 |
| 2 | Energy saving | 2,17,953 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹29,35,826 |
| 5 | Estimated investment | ₹10,00,000 |
| 6 | Payback period (years) | 34 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.4.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.4.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.4.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.4.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.4.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.4.15 Benefits Other Than Energy Saving

• Raising chilled water supply temperature improves chiller COP/efficiency and reduces compressor power consumption. No major capital cost. Quick payback.

| Benefit | Description |
| --- | --- |

### 3.4.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.4.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.4.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.5 ECM 5 – Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand

### 3.5.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand |
| Project number | ECM 5 |
| System | Chiller Plant Automation and Sequencing |
| Location | To be updated |
| Equipment covered | Chiller Plant Manager |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 8,56,615 kWh/year |
| Expected annual cost saving | ₹1,15,38,605 |
| Estimated investment | ₹60,00,000 |
| Simple payback period | 52 years |
| Implementation duration | To be updated |
| Implementation priority | I |

### 3.5.2 Existing System Description

• 1000 TR Centrifugal Chiller (Mall) x 3 Nos. (Without VFD) 2. 500 TR Centrifugal Chiller (Cinema) x 1 No. (Without VFD) 3. 1629 TR Cooling Tower (Mall) x 3 Nos. (Without VFD) 4. 676 TR Cooling Tower (Cinema) x 1 No. (Without VFD) 5. 30 kW Primary Pump (Mall) x 4 Nos. (Without VFD) 6. 15 kW Primary Pump (Cinema) x 2 Nos. (Without VFD) 7. 37 kW Seconadry Pump (Mall) x 5 Nos. (With VFD) 8. 22 kW Seconadry Pump (Cinema) x 2 Nos. (With VFD) 9. 75 kW Condenser Pump (Mall) x 4 Nos. (Without VFD) 10. 30 kW Condenser Pump (Cinema) x 2 Nos. (Without VFD) Additional Notes: Put VFDs on all pumps, motors and sensor along with chiller controller

### 3.5.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 7138459 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.5.4 Problem / Gap Identified

• Cooling load varies significantly across summer, monsoon, winter seasons and process demand. Existing system operates with fixed-speed chillers, cooling towers and primary pumps, resulting in part-load inefficiencies, excess pumping power and sub-optimal condenser pressure control.

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.5.5 Proposed Project

• Optimization of chiller plant operation through automated chiller sequencing, PRV optimization, condenser water temperature control, and primary/secondary pump flow optimization based on actual cooling demand

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.5.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.5.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.5.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 8,56,615 |
| Annual cost saving | ₹/year | ₹1,15,38,605 |
| Estimated investment | ₹ | ₹60,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.5.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 7138459 |
| 2 | Energy saving | 8,56,615 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,15,38,605 |
| 5 | Estimated investment | ₹60,00,000 |
| 6 | Payback period (years) | 52 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.5.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.5.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.5.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.5.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.5.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.5.15 Benefits Other Than Energy Saving

• Reduces overall chiller plant kW/TR through intelligent automation, optimized equipment sequencing, dynamic setpoint control, condenser optimization and demand-based pumping operation. Improves system stability, reduces over-pumping and enhances part-load performance.

| Benefit | Description |
| --- | --- |

### 3.5.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.5.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.5.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.6 ECM 6 – Condenser pump motor retrofit with high efficiency motor (IE4/IE5) with VFD and ΔT & ΔP automation

### 3.6.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Condenser pump motor retrofit with high efficiency motor (IE4/IE5) with VFD and ΔT & ΔP automation |
| Project number | ECM 6 |
| System | Condenser Water Pumping System |
| Location | To be updated |
| Equipment covered | Condenser Pump 1 & 3 |
| Existing operating condition | The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load. |
| Proposed intervention | The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load. |
| Expected energy saving | 60,366 kWh/year |
| Expected annual cost saving | ₹8,13,133 |
| Estimated investment | ₹15,93,000 |
| Simple payback period | 96 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.6.2 Existing System Description

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

### 3.6.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 603662 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.6.4 Problem / Gap Identified

• Cooling Load significantly varrying with season and variation in cooling requirement

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.6.5 Proposed Project

• Condenser pump motor retrofit with high efficiency motor (IE4/IE5) with VFD and ΔT & ΔP automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.6.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.6.7 Rationale for Energy Saving

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.6.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 60,366 |
| Annual cost saving | ₹/year | ₹8,13,133 |
| Estimated investment | ₹ | ₹15,93,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.6.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 603662 |
| 2 | Energy saving | 60,366 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹8,13,133 |
| 5 | Estimated investment | ₹15,93,000 |
| 6 | Payback period (years) | 96 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.6.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.6.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.6.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.6.13 Precautions / Aspects to be Taken Care Of

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.6.14 Measurement and Verification Plan

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.6.15 Benefits Other Than Energy Saving

• Upgrade the condenser pump motor with a high-efficiency IE4/IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 4–6%.

| Benefit | Description |
| --- | --- |

### 3.6.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.6.17 Case Study / Reference Application

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

### 3.6.18 Project Conclusion

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

3.7 ECM 7 – Primary pump motor retrofit with high efficiency motor IE5 with VFD and ΔT & ΔP automation

### 3.7.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Primary pump motor retrofit with high efficiency motor IE5 with VFD and ΔT & ΔP automation |
| Project number | ECM 7 |
| System | Primary CHW Pumping System |
| Location | To be updated |
| Equipment covered | Primary Pump 1, 2 & 3 |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 47,997 kWh/year |
| Expected annual cost saving | ₹6,46,523 |
| Estimated investment | ₹13,50,000 |
| Simple payback period | 9 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.7.2 Existing System Description

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.7.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 399977 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.7.4 Problem / Gap Identified

• Cooling Load significantly varrying with season and variation in cooling requirement

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.7.5 Proposed Project

• Primary pump motor retrofit with high efficiency motor IE5 with VFD and ΔT & ΔP automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.7.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.7.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.7.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 47,997 |
| Annual cost saving | ₹/year | ₹6,46,523 |
| Estimated investment | ₹ | ₹13,50,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.7.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 399977 |
| 2 | Energy saving | 47,997 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹6,46,523 |
| 5 | Estimated investment | ₹13,50,000 |
| 6 | Payback period (years) | 9 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.7.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.7.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.7.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.7.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.7.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.7.15 Benefits Other Than Energy Saving

• Upgrade the condenser pump motor with a high-efficiency IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 10 to 12%.

| Benefit | Description |
| --- | --- |

### 3.7.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.7.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.7.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.8 ECM 8 – Secondary pump motor retrofit with high efficiency motor IE5 with existing VFD and ΔT & ΔP automation

### 3.8.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Secondary pump motor retrofit with high efficiency motor IE5 with existing VFD and ΔT & ΔP automation |
| Project number | ECM 8 |
| System | Secondary CHW Pumping System |
| Location | To be updated |
| Equipment covered | Secondary Pump 1, 3, & 2(C) |
| Existing operating condition | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Proposed intervention | The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance. |
| Expected energy saving | 45,745 kWh/year |
| Expected annual cost saving | ₹6,16,181 |
| Estimated investment | ₹14,25,000 |
| Simple payback period | 31 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.8.2 Existing System Description

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.8.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 381206 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.8.4 Problem / Gap Identified

• Cooling Load significantly varrying with season and variation in cooling requirement

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.8.5 Proposed Project

• Secondary pump motor retrofit with high efficiency motor IE5 with existing VFD and ΔT & ΔP automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.8.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.8.7 Rationale for Energy Saving

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.8.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 45,745 |
| Annual cost saving | ₹/year | ₹6,16,181 |
| Estimated investment | ₹ | ₹14,25,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.8.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 381206 |
| 2 | Energy saving | 45,745 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹6,16,181 |
| 5 | Estimated investment | ₹14,25,000 |
| 6 | Payback period (years) | 31 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.8.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.8.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.8.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.8.13 Precautions / Aspects to be Taken Care Of

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.8.14 Measurement and Verification Plan

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.8.15 Benefits Other Than Energy Saving

• Upgrade the condenser pump motor with a high-efficiency IE5 motor along with VFD and ΔT & ΔP-based automation to match pump operation with varying cooling load. This ensures optimized flow, reduces energy consumption, and improves system efficiency, with expected savings of 10%.

| Benefit | Description |
| --- | --- |

### 3.8.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.8.17 Case Study / Reference Application

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

### 3.8.18 Project Conclusion

• The existing cooling system includes equipment operating under conditions where flow, temperature differential, and load variation require verification for optimized energy performance.

3.9 ECM 9 – Existing IE2 efficiency class retrofit with high efficiency motor (IE5) and cogged belt

### 3.9.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Existing IE2 efficiency class retrofit with high efficiency motor (IE5) and cogged belt |
| Project number | ECM 9 |
| System | STP Blower / Motor Drive System |
| Location | To be updated |
| Equipment covered | Air Blower (STP) |
| Existing operating condition | The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load. |
| Proposed intervention | The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load. |
| Expected energy saving | 17,520 kWh/year |
| Expected annual cost saving | ₹2,35,994 |
| Estimated investment | ₹4,00,000 |
| Simple payback period | 69 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.9.2 Existing System Description

• IE5 Efficiency class motor with VFD (22 kW, 4 Pole, Mounting: foot, frame size: 180L

### 3.9.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 87600 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.9.4 Problem / Gap Identified

• Upgrading from an IE2 to IE5 motor significantly improves motor efficiency, reducing electrical losses. Additionally, replacing the conventional belt with a cogged belt minimizes transmission losses and slippage, ensuring better power transfer. This results in lower energy consumption and improved overall blower performance

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.9.5 Proposed Project

• Existing IE2 efficiency class retrofit with high efficiency motor (IE5) and cogged belt

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.9.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.9.7 Rationale for Energy Saving

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.9.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 17,520 |
| Annual cost saving | ₹/year | ₹2,35,994 |
| Estimated investment | ₹ | ₹4,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.9.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 87600 |
| 2 | Energy saving | 17,520 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,35,994 |
| 5 | Estimated investment | ₹4,00,000 |
| 6 | Payback period (years) | 69 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.9.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.9.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.9.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.9.13 Precautions / Aspects to be Taken Care Of

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.9.14 Measurement and Verification Plan

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.9.15 Benefits Other Than Energy Saving

• Upgrade the existing IE2 motor to a high-efficiency IE5 motor and replace the conventional belt with a cogged belt to improve power transmission and reduce losses with DO sensors. This enhances overall blower efficiency and reduces energy consumption

| Benefit | Description |
| --- | --- |

### 3.9.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.9.17 Case Study / Reference Application

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

### 3.9.18 Project Conclusion

• The existing driven equipment is operated by standard-efficiency motors, resulting in higher power consumption for the given mechanical load.

3.10 ECM 10 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

### 3.10.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| Project number | ECM 10 |
| System | AHU Plug Fan System |
| Location | To be updated |
| Equipment covered | Air Handling Unit (12 Nos) |
| Existing operating condition | The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades. |
| Proposed intervention | The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades. |
| Expected energy saving | 91,330 kWh/year |
| Expected annual cost saving | ₹12,30,215 |
| Estimated investment | ₹27,82,546 |
| Simple payback period | 26 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.10.2 Existing System Description

• YEARLY AHU kWh CONSUMPTION 1. AHU 01 GF (15,000cfm@65mmwg) - 20,468 kWh/year 2. AHU 02 GF (24,000cfm@65mmwg) - 20,135 kWh/year 3. AHU 03 GF (19,000cfm@65mmwg) - 13,140 kWh/year 4. AHU 01 1F (10,000cfm@65mmwg) - 12,099 kWh/year 5. AHU 02 1F (10,000cfm@65mmwg) - 6,456 kWh/year 6. AHU 03 1F (10,000cfm@65mmwg)- 15,196 kWh/year 7. AHU 01 2F (10,000cfm@65mmwg) - 7,450 kWh/year 8. AHU 02 2F (10,000cfm@65mmwg) - 13,815 kWh/year 9. AHU 03 2F (10,000cfm@65mmwg) - 15,201 kWh/year 10. AHU 01 Terrace (22,200cfm@65mmwg) - 22,500 kWh/year 11. AHU 02 Terrace (24,000cfm@65mmwg) - 33,875 kWh/year 12.AHU 03 Terrace (22,200cfm@65mmwg) - 32,660 kWh/year

### 3.10.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 228325 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.10.4 Problem / Gap Identified

• Belt driven fan, IE2 efficincy motor

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.10.5 Proposed Project

• Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.10.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.10.7 Rationale for Energy Saving

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.10.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 91,330 |
| Annual cost saving | ₹/year | ₹12,30,215 |
| Estimated investment | ₹ | ₹27,82,546 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.10.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 228325 |
| 2 | Energy saving | 91,330 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹12,30,215 |
| 5 | Estimated investment | ₹27,82,546 |
| 6 | Payback period (years) | 26 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.10.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.10.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.10.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.10.13 Precautions / Aspects to be Taken Care Of

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.10.14 Measurement and Verification Plan

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Airflow, static pressure, fan kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.10.15 Benefits Other Than Energy Saving

• Replacement of belt-driven blowers with direct-driven aerofoil plug fans equipped with IE5 high-efficiency motors significantly reduces transmission losses and improves overall system efficiency. The elimination of belts minimizes maintenance, improves reliability, and ensures consistent airflow. Automation further optimizes energy usage by adjusting fan speed based on demand, leading to substantial power savings and improved system performance.

| Benefit | Description |
| --- | --- |

### 3.10.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.10.17 Case Study / Reference Application

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

### 3.10.18 Project Conclusion

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

3.11 ECM 11 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

### 3.11.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| Project number | ECM 11 |
| System | Air Washer Plug Fan System |
| Location | To be updated |
| Equipment covered | Air Washer |
| Existing operating condition | The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades. |
| Proposed intervention | The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades. |
| Expected energy saving | 63,630 kWh/year |
| Expected annual cost saving | ₹8,57,091 |
| Estimated investment | ₹23,13,031 |
| Simple payback period | 70 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.11.2 Existing System Description

• YEARLY AIR -WASHER kWh CONSUMPTION 1. Air Washer 01 Terrace - OFF 2. Air Washer 02 Terrace (3,700cfm@60mmwg) - 5,310 kWh/year 3. Air Washer 03 Terrace (14,500cfm@60mmwg) - 17,248 kWh/year 4. Air Washer 04 Terrace (14,500cfm@60mmwg) - 25,297 kWh/year 5. Air Washer 05 Terrace - OFF 6. Air Washer 06 Terrace (14,500cfm@60mmwg) - 31,532 kWh/year 7. Air Washer 07 Terrace (22,000cfm@60mmwg) - 10,527 kWh/year 8. Air Washer 08 Terrace (22,000cfm@60mmwg) - 20,012 kWh/year 9. Air Washer 09 Terrace (22,200cfm@60mmwg) - 28,696 kWh/year 10. Air Washer 10 Terrace (26,000cfm@60mmwg) - 20,452 kWh/year

### 3.11.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 159074 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.11.4 Problem / Gap Identified

• Belt driven fan, IE2 efficiency motor

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.11.5 Proposed Project

• Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.11.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.11.7 Rationale for Energy Saving

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.11.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 63,630 |
| Annual cost saving | ₹/year | ₹8,57,091 |
| Estimated investment | ₹ | ₹23,13,031 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.11.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 159074 |
| 2 | Energy saving | 63,630 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹8,57,091 |
| 5 | Estimated investment | ₹23,13,031 |
| 6 | Payback period (years) | 70 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.11.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.11.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.11.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.11.13 Precautions / Aspects to be Taken Care Of

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.11.14 Measurement and Verification Plan

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Airflow, static pressure, fan kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.11.15 Benefits Other Than Energy Saving

• Upgrading to direct-driven aerofoil plug fans with IE5 motors eliminates belt losses and enhances airflow efficiency. The system benefits from reduced power consumption, lower maintenance requirements, and improved operational stability. Automation enables demand-based control, resulting in optimized energy utilization and improved environmental control.

| Benefit | Description |
| --- | --- |

### 3.11.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.11.17 Case Study / Reference Application

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

### 3.11.18 Project Conclusion

• The existing air handling system operates with conventional fan and drive arrangements, presenting opportunities for flow optimization and efficiency upgrades.

3.12 ECM 12 – Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

### 3.12.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation |
| Project number | ECM 12 |
| System | Heat Recovery Wheel / Ventilation Fan System |
| Location | To be updated |
| Equipment covered | HRW (Heat Recovery Wheel) |
| Existing operating condition | The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact. |
| Proposed intervention | The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact. |
| Expected energy saving | 1,78,858 kWh/year |
| Expected annual cost saving | ₹24,09,217 |
| Estimated investment | ₹36,41,850 |
| Simple payback period | 51 years |
| Implementation duration | To be updated |
| Implementation priority | II |

### 3.12.2 Existing System Description

• YEARLY HRW kWh CONSUMPTION 1.1. Heat Recovery Wheel Fresh Air 1 (26,000cfm@50mmwg) - 60,468 kWh/Year 1.1. Heat Recovery Wheel Exhaust Air 1 (20,800cfm@50mmwg) - 36,290 kWh/Year 2.1. Heat Recovery Wheel Fresh Air 2 (26,000cfm@50mmwg) - 38,719 kWh/Year 2.2. Heat Recovery Wheel Exhaust Air 2 - OFF 3.1. Heat Recovery Wheel Fresh Air 3 (26,000cfm@50mmwg) - 48,779 kWh/Year 3.2. Heat Recovery Wheel Exhaust Air 3 (26,000cfm@50mmwg) - 47,479 kWh/Year 4.1. Heat Recovery Wheel Fresh Air 4 (24,000cfm@50mmwg) - 31,155 kWh/Year 4.2. Heat Recovery Wheel Exhaust Air 4 - OFF 5.1. Heat Recovery Wheel Fresh Air 5 (21,500cfm@50mmwg) - 36,494 kWh/Year 5.2. Heat Recovery Wheel Exhaust Air 5 - OFF 6.1. Heat Recovery Wheel Fresh Air 6 (24,000cfm@50mmwg) - 27,975 kWh/Year 6.2. Heat Recovery Wheel Exhaust Air 6 - OFF 7.1. Heat Recovery Wheel Fresh Air 7 (24,000cfm@50mmwg) - 46,246 kWh/Year 7.2. Heat Recovery Wheel Exhaust Air 7 - OFF 8.1. Heat Recovery Wheel Fresh Air 8 (17,000cfm@50mmwg) - 38,448 kWh/Year 8.2. Heat Recovery Wheel Exhaust Air 8 - OFF 9.1. Heat Recovery Wheel Fresh Air 9 (17,000cfm@50mmwg) - 35,093 kWh/Year 9.2. Heat Recovery Wheel Exhaust Air 9 - OFF

### 3.12.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 447145 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.12.4 Problem / Gap Identified

• Belt driven fan, IE2 efficiency motor

| System | Typical Gap |
| --- | --- |
| APFC | Low PF or kVAh billing loss |

### 3.12.5 Proposed Project

• Belt driven blower retrofit with direct driven aerofoil section plug fan with high efficiency motor (IE5) and automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.12.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.12.7 Rationale for Energy Saving

• The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact.

| Project Type | Saving Rationale |
| --- | --- |
| APFC | To be updated |

### 3.12.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 1,78,858 |
| Annual cost saving | ₹/year | ₹24,09,217 |
| Estimated investment | ₹ | ₹36,41,850 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.12.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 447145 |
| 2 | Energy saving | 1,78,858 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹24,09,217 |
| 5 | Estimated investment | ₹36,41,850 |
| 6 | Payback period (years) | 51 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.12.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.12.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.12.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.12.13 Precautions / Aspects to be Taken Care Of

• The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.12.14 Measurement and Verification Plan

• The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | PF, kVA, kVAh, reactive power compensation | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.12.15 Benefits Other Than Energy Saving

• Upgrading to direct-driven aerofoil plug fans with IE5 motors eliminates belt losses and enhances airflow efficiency. The system benefits from reduced power consumption, lower maintenance requirements, and improved operational stability. Automation enables demand-based control, resulting in optimized energy utilization and improved environmental control.

| Benefit | Description |
| --- | --- |

### 3.12.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.12.17 Case Study / Reference Application

• The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact.

### 3.12.18 Project Conclusion

• The electrical system requires effective reactive power compensation to maintain power factor and reduce kVA/kVAh-related billing impact.

3.13 ECM 13 – Scrubber motor retrofit with high efficiency motor with VFD and DCV automation

### 3.13.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Scrubber motor retrofit with high efficiency motor with VFD and DCV automation |
| Project number | ECM 13 |
| System | Scrubber Ventilation Motor System |
| Location | To be updated |
| Equipment covered | Srubber Unit |
| Existing operating condition | The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy. |
| Proposed intervention | The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy. |
| Expected energy saving | 82,442 kWh/year |
| Expected annual cost saving | ₹11,10,487 |
| Estimated investment | ₹22,00,000 |
| Simple payback period | 98 years |
| Implementation duration | To be updated |
| Implementation priority | To be updated |

### 3.13.2 Existing System Description

• YEARLY SCRUBBER kWh CONSUMPTION 1. Scrubber 01 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM)- 40686 kWh/Year 2. Scrubber 02 Terrace (4,600cfm@70mmwg, 3.7kW, 1500 RPM) - 11,826 kWh/Year 3. Scrubber 03 Terrace (17,800cfm@70mmwg, 11kW, 1500 RPM) - 38,982 kWh/Year 4. Scrubber 04 Terrace (17,800cfm@70mmwg, 11kW, 1500 RPM) - 26,017 kWh/Year 5. Scrubber 05 Terrace (17,800cfm@60mmwg, 7.5kW, 1500 RPM) - 21,854 kWh/Year 6. Scrubber 06 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 39,902 kWh/Year 7. Scrubber 07 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 37,935 kWh/Year 8. Scrubber 08 Terrace (17,800cfm@60mmwg, 7.5kW, 1500 RPM) - 39,823 kWh/Year 9. Scrubber 09 Terrace (26,200cfm@60mmwg, 15kW, 1500 RPM) - 49,363 kWh/Year 10. Scrubber 10 Terrace (24,700cfm@50mmwg, 7.5kW, 1500 RPM) - 23,378 kWh/Year

### 3.13.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 329766 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.13.4 Problem / Gap Identified

• IE2 efficincy class motor and no automation

| System | Typical Gap |
| --- | --- |
| Heat recovery | Waste heat discharged without useful recovery |

### 3.13.5 Proposed Project

• Scrubber motor retrofit with high efficiency motor with VFD and DCV automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.13.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.13.7 Rationale for Energy Saving

• The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy.

| Project Type | Saving Rationale |
| --- | --- |
| Heat recovery | To be updated |

### 3.13.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 82,442 |
| Annual cost saving | ₹/year | ₹11,10,487 |
| Estimated investment | ₹ | ₹22,00,000 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.13.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 329766 |
| 2 | Energy saving | 82,442 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹11,10,487 |
| 5 | Estimated investment | ₹22,00,000 |
| 6 | Payback period (years) | 98 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.13.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.13.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.13.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.13.13 Precautions / Aspects to be Taken Care Of

• The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.13.14 Measurement and Verification Plan

• The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Exhaust air temperature, inlet air temperature, heater kW, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.13.15 Benefits Other Than Energy Saving

• Upgrading scrubber motors to high-efficiency IE5 motors with VFD and DCV (Demand Control Ventilation) improves energy efficiency by matching motor speed with process requirements. This reduces unnecessary power consumption, enhances process control, and extends equipment life while lowering maintenance costs.

| Benefit | Description |
| --- | --- |

### 3.13.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.13.17 Case Study / Reference Application

• The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy.

### 3.13.18 Project Conclusion

• The existing dryer system rejects usable heat through exhaust air, while incoming regeneration air continues to require primary heating energy.

3.14 ECM 18 – Energy Saving in Chiller by improving operational practices

### 3.14.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Energy Saving in Chiller by improving operational practices |
| Project number | ECM 18 |
| System | Chiller Operational Practice Improvement |
| Location | To be updated |
| Equipment covered | Chiller |
| Existing operating condition | The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle. |
| Proposed intervention | The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle. |
| Expected energy saving | 1,82,441 kWh/year |
| Expected annual cost saving | ₹24,57,483 |
| Estimated investment | ₹0 |
| Simple payback period | 0 years |
| Implementation duration | To be updated |
| Implementation priority | To be updated |

### 3.14.2 Existing System Description

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

### 3.14.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | To be updated |
| Quantity | Nos. | To be updated |
| Operating hours | hours/day | To be updated |
| Operating days | days/year | To be updated |
| Existing power consumption | kW | To be updated |
| Annual operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | 5448824 |
| Average tariff | ₹/kWh | To be updated |
| Baseline annual energy cost | ₹/year | To be updated |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | To be updated |
| Current | A | To be updated |
| Power factor | - | To be updated |
| Measured power | kW | To be updated |
| Flow / airflow | m3/hr / CFM | To be updated |
| Pressure / head / static pressure | m / mmWC / bar | To be updated |
| Temperature inlet | °C | To be updated |
| Temperature outlet | °C | To be updated |
| Operating frequency | Hz | To be updated |

### 3.14.4 Problem / Gap Identified

• Cooling tower approach is high, causing the chiller condenser cooling water temperature to reach (WBT + 5°C), which is excessive and resulting in higher chiller power consumption

| System | Typical Gap |
| --- | --- |
| System | To be updated |

### 3.14.5 Proposed Project

• Energy Saving in Chiller by improving operational practices

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.14.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |

### 3.14.7 Rationale for Energy Saving

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

| Project Type | Saving Rationale |
| --- | --- |
| Project | To be updated |

### 3.14.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment quantity | Nos | To be updated |
| Existing connected load / measured load | kW | To be updated |
| Operating hours | hours/year | To be updated |
| Baseline annual consumption | kWh/year | To be updated |
| Annual energy saving | kWh/year | 1,82,441 |
| Annual cost saving | ₹/year | ₹24,57,483 |
| Estimated investment | ₹ | ₹0 |
| Simple payback | years | NaN |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.14.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 5448824 |
| 2 | Energy saving | 1,82,441 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹24,57,483 |
| 5 | Estimated investment | ₹0 |
| 6 | Payback period (years) | 0 |
| 7 | CO2 reduction | [Calculation pending] |

### 3.14.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | To be updated |
| Capacity | To be updated |
| Quantity | To be updated |
| Motor efficiency class, if applicable | To be updated |
| VFD rating, if applicable | To be updated |
| Sensor type | To be updated |
| Controller / PLC / IoT system | To be updated |
| Communication | To be updated |
| Panel requirement | To be updated |
| Civil / mechanical modification | To be updated |
| Safety requirement | To be updated |

### 3.14.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.14.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and approval | 1 week |
| Procurement | 2-4 weeks |
| Installation | 1-2 weeks |
| Testing and commissioning | 1 week |
| Performance monitoring | 2-4 weeks |
| Total expected duration | To be updated |

### 3.14.13 Precautions / Aspects to be Taken Care Of

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.14.14 Measurement and Verification Plan

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.14.15 Benefits Other Than Energy Saving

• Use 2 CTs for 1 Chiller 2. Use 3 CTs for 2 Chiller 3. Use 4 CTs for 3 Chiller (For every 1°C reduction in condenser water temperature, the chiller compressor power consumption decreases by approximately 2% to 3%).

| Benefit | Description |
| --- | --- |

### 3.14.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.14.17 Case Study / Reference Application

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

### 3.14.18 Project Conclusion

• The existing hydraulic machine drive arrangement operates with energy consumption during idle and part-load portions of the machine cycle.

# Chapter 4: Annexures

## 4.1 Uploaded Data Sources

Uploaded spreadsheets, measurements, and supporting documents used for this report are referenced here.

## 4.2 Assumptions

Savings, investment, and implementation assumptions are based on the data made available during the audit and SEE-Tech engineering judgment where direct readings were not available.

## 4.3 Image / Figure References

Photographs, schematics, and reference figures included in the report are listed in this section.

## 4.4 Calculation Notes

Calculation notes, formulas, and validation references supporting the ECM analysis are documented here.