SEE-Tech Solutions

Commercial Building Energy Audit Report Format

Detailed Energy Audit Report

Purpose: To identify implementable energy-saving projects with clear investment, savings, payback and execution roadmap.

| Prepared For | MTL Baddi |
| --- | --- |
| Building Type | Industrial Facility |
| Location | Baddi |
| Audit Period | 2026-05 |
| Report Date |  |
| Prepared By | SEE-Tech Solutions |
| Document Version | Draft |

# Table of Contents

Chapter 1. Executive Summary

1.1 Purpose of the Energy Audit

1.2 Overall Energy Saving Potential

1.3 Summary of Identified Energy Saving Projects

1.4 Project Grouping

1.5 Key Observations

1.6 Recommended Implementation Priority

1.7 Conclusion and Way Forward

Chapter 2. Plant / Building Details and Energy Profile

2.1 General Information

2.2 Building Operation Details

2.3 Utility and Energy Sources

2.4 Electrical Supply Details

2.5 Electricity Consumption and Billing Summary

2.6 Specific Energy Consumption Benchmark

2.7 Major Energy Consuming Systems

2.8 HVAC System Details

2.9 Lighting System Details

2.10 Pumps and Motors

2.11 Building Automation and Controls

2.12 Summary of Audit Observations

Chapter 3. Energy Saving Projects

GR-1 Cooling System Performance Improvement

3.1 ECM 1 – EE Improvement in Chiller Using CT Segregation

3.2 ECM 2 – Flow Optimization for CHW Secondary Pump

3.3 ECM 3 – EE Improvement in Air Compressors & Pump Using CT Segregation

3.4 ECM 4 – Automatic Primary Pump Flow Control for Chiller kW/TR Optimization

3.5 ECM 5 – Free Cooling by Chiller Bypass in Winter

3.6 ECM 8 – IE5 Efficiency Motor Retrofit for CHW Secondary Pump

3.7 ECM 9 – IE5 Efficiency Motor Retrofit for CT Water Secondary Pump

GR-2 Production Machines

3.8 ECM 13 – Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers

3.9 ECM 14 – Insulation hot flexible ducts (72 Nos)

3.10 ECM 15 – Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos)

3.11 ECM 16 – ASB 70 DPH (7 Nos) Servo Motor Project

3.12 ECM 17 – ASB 50 MB (18 Nos) Servo Motor Project

3.13 ECM 18 – EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project

3.14 ECM 19 – EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project

3.15 ECM 20 – EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project

GR-3 Air Compressors

3.16 ECM 21 – Compressed Air Measurement & Management

3.17 ECM 22 – Booster Compressor retrofit with IE5 Efficiency motor & automation

GR-4 Auxiliary Systems & Machine Improvement

3.18 ECM 6 – CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit

3.19 ECM 7 – Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans

3.20 ECM 10 – Cutting Grinders Retrofit with IE5 Motor & Cogged belt

3.21 ECM 11 – PD blower Direct Mounting with IE5 motor with existing VFD

3.22 ECM 12 – APFC relay for 600 kVAr Panel

Chapter 4. Annexures

# Chapter 1: Executive Summary

## 1.1 Purpose of the Energy Audit

The detailed energy audit identifies energy conservation measures directly from the uploaded Excel workbook and evaluates them for technical feasibility, implementation practicality, and financial attractiveness.

## 1.2 Overall Energy Saving Potential

| Particular | Value |
| --- | --- |
| Total annual electricity consumption |  |
| Annual electricity cost |  |
| Average electricity tariff considered |  |
| Number of projects identified | 22 |
| Total energy saving potential | 19,02,387 |
| Total annual cost saving potential | ₹1,36,40,112 |
| Total estimated investment | ₹2,49,43,149 |
| Simple payback period | 1.83 |
| CO2 reduction potential | [Calculation pending due to missing emission factor] |

## 1.3 Summary of Identified Energy Saving Projects

| ECM No. | Energy Saving Project | System | Investment | Annual Saving | Energy Saving kWh/y |
| --- | --- | --- | --- | --- | --- |
| ECM 1 | EE Improvement in Chiller Using CT Segregation | Utility | ₹3,50,000 | ₹2,30,355 | 32,128 |
| ECM 2 | Flow Optimization for CHW Secondary Pump | Utility | ₹1,50,000 | ₹1,27,102 | 17,727 |
| ECM 3 | EE Improvement in Air Compressors & Pump Using CT Segregation | Utility | ₹4,50,000 | ₹10,34,106 | 1,44,227 |
| ECM 4 | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization | Utility | ₹1,45,000 | ₹3,28,615 | 45,832 |
| ECM 5 | Free Cooling by Chiller Bypass in Winter | Utilty | ₹5,00,000 | ₹4,30,200 | 60,000 |
| ECM 6 | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit | Utility | ₹4,88,750 | ₹1,76,561 | 24,625 |
| ECM 7 | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans | Utility | ₹3,10,000 | ₹1,40,543 | 19,602 |
| ECM 8 | IE5 Efficiency Motor Retrofit for CHW Secondary Pump | Utility | ₹2,70,000 | ₹1,83,665 | 25,616 |
| ECM 9 | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump | Utility | ₹10,11,933 | ₹3,74,832 | 52,278 |
| ECM 10 | Cutting Grinders Retrofit with IE5 Motor & Cogged belt | Process | ₹4,88,599 | ₹2,00,760 | 28,000 |
| ECM 11 | PD blower Direct Mounting with IE5 motor with existing VFD | Process | ₹2,70,000 | ₹1,24,220 | 17,325 |
| ECM 12 | APFC relay for 600 kVAr Panel | Utility | ₹50,000 | ₹12,11,273 | 1,68,936 |
| ECM 13 | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers | ISBM | ₹10,50,000 | ₹3,92,342 | 54,720 |
| ECM 14 | Insulation hot flexible ducts (72 Nos) | ISBM | ₹7,40,000 | ₹14,32,566 | 1,99,800 |
| ECM 15 | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) | ISBM | ₹8,50,000 | ₹2,81,064 | 39,200 |
| ECM 16 | ASB 70 DPH (7 Nos) Servo Motor Project | ISBM | ₹52,50,000 | ₹19,39,535 | 2,70,507 |
| ECM 17 | ASB 50 MB (18 Nos) Servo Motor Project | ISBM | ₹90,00,000 | ₹30,55,386 | 4,26,135 |
| ECM 18 | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project | EBM | ₹10,00,000 | ₹3,44,075 | 47,988 |
| ECM 19 | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project | EBM | ₹6,00,000 | ₹2,01,857 | 28,153 |
| ECM 20 | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project | EBM | ₹9,10,000 | ₹2,71,590 | 37,879 |
| ECM 21 | Compressed Air Measurement & Management | Utility | ₹8,00,000 | ₹10,54,166 | 1,47,025 |
| ECM 22 | Booster Compressor retrofit with IE5 Efficiency motor & automation | Utility | ₹2,58,868 | ₹1,05,299 | 14,686 |

## 1.4 Project Grouping

The identified Energy Conservation Measures (ECMs) are grouped into technical and functional categories below to facilitate structured implementation and system-level improvements.

| Group No. | Group Name | ECMs Included | No. of ECMs | Total Investment | Annual Saving | Energy Saving | Group Payback |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GR-1 | GR-1 Cooling System Performance Improvement | ECM 1, ECM 2, ECM 3, ECM 4, ECM 5, ECM 8, ECM 9 | 7 | ₹28,76,933 | ₹27,08,874 | 3,77,807 | 1.06 |
| GR-2 | GR-2 Production Machines | ECM 13, ECM 14, ECM 15, ECM 16, ECM 17, ECM 18, ECM 19, ECM 20 | 8 | ₹1,94,00,000 | ₹79,18,416 | 11,04,382 | 2.45 |
| GR-3 | GR-3 Air Compressors | ECM 21, ECM 22 | 2 | ₹10,58,868 | ₹11,59,465 | 1,61,711 | 0.91 |
| GR-4 | GR-4 Auxiliary Systems & Machine Improvement | ECM 6, ECM 7, ECM 10, ECM 11, ECM 12 | 5 | ₹16,07,349 | ₹18,53,358 | 2,58,488 | 0.87 |

## 1.5 Key Observations

Cooling System Performance Improvement includes 7 ECMs with combined annual saving of 2708873.8958999994.

Production Machines includes 8 ECMs with combined annual saving of 7918415.8314000005.

Air Compressors includes 2 ECMs with combined annual saving of 1159465.0019999999.

Auxiliary Systems & Machine Improvement includes 5 ECMs with combined annual saving of 1853357.526.

## 1.6 Recommended Implementation Priority

Projects have been classified into High, Medium, and Long-Term priorities based on payback duration and implementation feasibility.

| Priority Level | ECM Numbers | Reason for Priority | Investment | Annual Saving | Payback | Implementation Note |
| --- | --- | --- | --- | --- | --- | --- |
| High Priority | ECM 2 | Favorable payback < 1.5 years | ₹1,50,000 | ₹1,27,102 | 1.18 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 3 | Favorable payback < 1.5 years | ₹4,50,000 | ₹10,34,106 | 0.44 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 4 | Favorable payback < 1.5 years | ₹1,45,000 | ₹3,28,615 | 0.44 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 5 | Favorable payback < 1.5 years | ₹5,00,000 | ₹4,30,200 | 1.16 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 8 | Favorable payback < 1.5 years | ₹2,70,000 | ₹1,83,665 | 1.47 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 12 | Favorable payback < 1.5 years | ₹50,000 | ₹12,11,273 | 0.04 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 14 | Favorable payback < 1.5 years | ₹7,40,000 | ₹14,32,566 | 0.52 | Implementation complexity to be finalized after site verification. |
| High Priority | ECM 21 | Favorable payback < 1.5 years | ₹8,00,000 | ₹10,54,166 | 0.76 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 1 | Moderate payback 1.5 - 3 years | ₹3,50,000 | ₹2,30,355 | 1.52 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 6 | Moderate payback 1.5 - 3 years | ₹4,88,750 | ₹1,76,561 | 2.77 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 7 | Moderate payback 1.5 - 3 years | ₹3,10,000 | ₹1,40,543 | 2.21 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 9 | Moderate payback 1.5 - 3 years | ₹10,11,933 | ₹3,74,832 | 2.7 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 10 | Moderate payback 1.5 - 3 years | ₹4,88,599 | ₹2,00,760 | 2.43 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 11 | Moderate payback 1.5 - 3 years | ₹2,70,000 | ₹1,24,220 | 2.17 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 13 | Moderate payback 1.5 - 3 years | ₹10,50,000 | ₹3,92,342 | 2.68 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 16 | Moderate payback 1.5 - 3 years | ₹52,50,000 | ₹19,39,535 | 2.71 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 17 | Moderate payback 1.5 - 3 years | ₹90,00,000 | ₹30,55,386 | 2.95 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 18 | Moderate payback 1.5 - 3 years | ₹10,00,000 | ₹3,44,075 | 2.91 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 19 | Moderate payback 1.5 - 3 years | ₹6,00,000 | ₹2,01,857 | 2.97 | Implementation complexity to be finalized after site verification. |
| Medium Priority | ECM 22 | Moderate payback 1.5 - 3 years | ₹2,58,868 | ₹1,05,299 | 2.46 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 15 | Longer payback or high capex | ₹8,50,000 | ₹2,81,064 | 3.02 | Implementation complexity to be finalized after site verification. |
| Long-Term Priority | ECM 20 | Longer payback or high capex | ₹9,10,000 | ₹2,71,590 | 3.35 | Implementation complexity to be finalized after site verification. |

## 1.7 Conclusion and Way Forward

Based on the audit findings, SEE-Tech recommends that MTL Baddi proceed with detailed implementation planning for the identified energy-saving projects. The suggested steps are:

| Step | Action |
| --- | --- |
| 1 | Site verification |
| 2 | Vendor quotation / detailed engineering |
| 3 | Implementation scheduling |
| 4 | M&V baseline confirmation |
| 5 | Execution |
| 6 | Post-implementation verification |

# Chapter 2: Plant / Building Details and Energy Profile

## 2.1 General Information

| Name of facility | MTL Baddi |
| --- | --- |
| Address | Baddi |
| Type of building | Industrial Facility |
| Year of construction | [To be updated after site data verification] |
| Total built-up area | [To be updated after site data verification] |
| Conditioned area | [To be updated after site data verification] |
| Number of floors | [To be updated after site data verification] |
| Occupancy type | [To be updated after site data verification] |
| Average occupancy | [To be updated after site data verification] |
| Operating days and hours | [To be updated after site data verification] |
| Facility contact person | Manager |
| Audit date | 2026-05 |
| SEE-Tech audit team | SEE-Tech Solutions |

## 2.2 Building Operation Details

| Area / Function | Operating Hours | Remarks |
| --- | --- | --- |
| Office area | [To be updated after site data verification] | [To be updated after site data verification] |
| Common area | [To be updated after site data verification] | [To be updated after site data verification] |
| Basement / parking | [To be updated after site data verification] | [To be updated after site data verification] |
| Server room / data room | [To be updated after site data verification] | [To be updated after site data verification] |
| Kitchen | [To be updated after site data verification] | [To be updated after site data verification] |
| Laundry | [To be updated after site data verification] | [To be updated after site data verification] |
| Guest rooms | [To be updated after site data verification] | [To be updated after site data verification] |
| Patient rooms / wards | [To be updated after site data verification] | [To be updated after site data verification] |
| OT / ICU / critical areas | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.3 Utility and Energy Sources

| Energy Source | Use | Annual Consumption | Annual Cost ₹ |
| --- | --- | --- | --- |
| Grid electricity | HVAC, lighting, pumps, plug loads | [To be updated after site data verification] | [To be updated after site data verification] |
| Diesel | DG backup | [To be updated after site data verification] | [To be updated after site data verification] |
| PNG / LPG | Kitchen, boiler, hot water | [To be updated after site data verification] | [To be updated after site data verification] |
| Solar PV | Captive generation | [To be updated after site data verification] | [To be updated after site data verification] |
| Solar thermal | Hot water | [To be updated after site data verification] | [To be updated after site data verification] |
| Other | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.4 Electrical Supply Details

| Supply voltage | [To be updated after site data verification] |
| --- | --- |
| Consumer number | [To be updated after site data verification] |
| Tariff category | [To be updated after site data verification] |
| Contract demand / sanctioned load | [To be updated after site data verification] |
| Connected load | [To be updated after site data verification] |
| Transformer capacity | [To be updated after site data verification] |
| DG capacity | [To be updated after site data verification] |
| APFC panel capacity | [To be updated after site data verification] |
| Average power factor | [To be updated after site data verification] |
| Billing type | [To be updated after site data verification] |
| Average electricity tariff | [To be updated after site data verification] |

## 2.5 Electricity Consumption and Billing Summary

| Month | kWh | kVAh | Maximum Demand kVA | PF | Bill Amount ₹ | Specific Consumption |
| --- | --- | --- | --- | --- | --- | --- |
| Apr | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| May | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Jun | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Jul | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Aug | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Sep | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Oct | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Nov | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Dec | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Jan | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Feb | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Mar | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Total / Average | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.6 Specific Energy Consumption Benchmark

| Building Type | Recommended Benchmark |
| --- | --- |
| Office building | kWh/sq.ft/year |
| IT park | kWh/sq.ft/year and kWh/workstation/year |
| Hotel | kWh/occupied room night |
| Hospital | kWh/bed/day or kWh/sq.ft/year |
| Mall | kWh/sq.ft/year |
| Educational building | kWh/student/year or kWh/sq.ft/year |

| Annual electricity consumption | [To be updated after site data verification] |
| --- | --- |
| Built-up area | [To be updated after site data verification] |
| Conditioned area | [To be updated after site data verification] |
| Annual occupancy / room nights / bed days | [To be updated after site data verification] |
| Specific energy consumption | [To be updated after site data verification] |
| Reference / target benchmark | [To be updated after site data verification] |
| Improvement potential | [To be updated after site data verification] |

## 2.7 Major Energy-Consuming Systems

| System | Major Equipment | Estimated Share of Energy Consumption | Remarks |
| --- | --- | --- | --- |
| HVAC | Chiller / VRF / AHU / pumps / cooling tower | [To be updated after site data verification] | [To be updated after site data verification] |
| Lighting | Indoor / outdoor / parking / facade | [To be updated after site data verification] | [To be updated after site data verification] |
| Pumps | Domestic / STP / hot water / HVAC | [To be updated after site data verification] | [To be updated after site data verification] |
| Plug loads | Office equipment / appliances | [To be updated after site data verification] | [To be updated after site data verification] |
| Server / IT loads | UPS, PAC, server room | [To be updated after site data verification] | [To be updated after site data verification] |
| Kitchen / laundry | Hotel / hospital loads | [To be updated after site data verification] | [To be updated after site data verification] |
| Hot water system | Boiler / heat pump / solar | [To be updated after site data verification] | [To be updated after site data verification] |
| Lifts / escalators | Vertical transport | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.8 HVAC System Details

| Equipment | Capacity | Quantity | Connected Load | Control System | Remarks |
| --- | --- | --- | --- | --- | --- |
| Chiller / VRF outdoor unit | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| AHU | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| FCU | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Cooling tower | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Chilled water pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Condenser water pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Fresh air unit | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Exhaust / ventilation fan | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

The HVAC system is one of the major energy-consuming systems in the building. During the audit, operating hours, loading pattern, temperature settings, pump and fan operation, control philosophy and maintenance condition should be reviewed. The main opportunities may relate to variable speed operation, AHU scheduling, chiller efficiency, fresh air optimization, cooling tower performance or set point optimization.

## 2.9 Lighting System Details

| Area | Existing Fixture | Wattage | Quantity | Operating Hours | Control Type |
| --- | --- | --- | --- | --- | --- |
| Office area | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Corridor | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Parking | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Outdoor | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Back-of-house | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Guest room / ward | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

Lighting energy consumption can be reduced through LED retrofit, lux optimization and occupancy-based controls. Corridors, parking areas, toilets, staircases and service areas are usually suitable for sensors or timer-based control.

## 2.10 Pumps and Motors

| Pump / Motor | Application | Rating kW | Quantity | Operating Hours | Control Method | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Domestic water pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Hydro-pneumatic pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| STP pump / blower | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Hot water pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| HVAC pump | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Exhaust fan | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.11 Building Automation and Controls

| System | Existing Control | Observation | Saving Opportunity |
| --- | --- | --- | --- |
| HVAC scheduling | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| AHU control | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Pump control | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Lighting control | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Parking ventilation | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Temperature set point | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |
| Energy monitoring | [To be updated after site data verification] | [To be updated after site data verification] | [To be updated after site data verification] |

## 2.12 Summary of Audit Observations

| Sr. No. | Observation | Impact | Recommended Project |
| --- | --- | --- | --- |
| 1 | [To be updated after site data verification] | High energy consumption | [To be updated after site data verification] |
| 2 | [To be updated after site data verification] | Higher demand / kVAh billing | [To be updated after site data verification] |
| 3 | [To be updated after site data verification] | Excess operating hours | [To be updated after site data verification] |
| 4 | [To be updated after site data verification] | Inefficient equipment | [To be updated after site data verification] |
| 5 | [To be updated after site data verification] | Poor control / manual operation | [To be updated after site data verification] |

# Chapter 3: Energy Saving Projects

This chapter presents the identified energy conservation measures grouped by system and application area. Each group includes a summary table followed by detailed ECM descriptions.

## GR-1 Cooling System Performance Improvement

This section covers 7 energy conservation measures under the Cooling System Performance Improvement category.

### Group Observation

### Implementation Focus

Implementation should combine site verification, detailed engineering, coordinated execution, and post-commissioning performance review.

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 1 | EE Improvement in Chiller Using CT Segregation | ₹3,50,000 | ₹2,30,355 | 32127.6 | 1.519394691 |
| ECM 2 | Flow Optimization for CHW Secondary Pump | ₹1,50,000 | ₹1,27,102 | 17726.85 | 1.180159029 |
| ECM 3 | EE Improvement in Air Compressors & Pump Using CT Segregation | ₹4,50,000 | ₹10,34,106 | 144226.71 | 0.4351586906 |
| ECM 4 | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization | ₹1,45,000 | ₹3,28,615 | 45831.9 | 0.4412462067 |
| ECM 5 | Free Cooling by Chiller Bypass in Winter | ₹5,00,000 | ₹4,30,200 | 60000 | 1.162250116 |
| ECM 8 | IE5 Efficiency Motor Retrofit for CHW Secondary Pump | ₹2,70,000 | ₹1,83,665 | 25615.8 | 1.470065497 |
| ECM 9 | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump | ₹10,11,933 | ₹3,74,832 | 52277.82 | 2.699697685 |

3.1 ECM 1 – EE Improvement in Chiller Using CT Segregation

### 3.1.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | EE Improvement in Chiller Using CT Segregation |
| Project number | ECM 1 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Chiller (1 No.) |
| Existing operating condition | Chiller Consumption is 3,21,276 kWh/Year |
| Proposed intervention | 1. VFD on dedicated CT Fan, 2. AI based Fan Speed Controller for all CT Fan 3. Dedicated Pump & Pipeline modification for Chiller Condenser Water with sensors & data display with cloud based data monitoring (Like BMS) |
| Expected energy saving | 32,128 kWh/year |
| Expected annual cost saving | ₹2,30,355 |
| Estimated investment | ₹3,50,000 |
| Simple payback period | 1.52 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.1.2 Existing System Description

Chiller Consumption is 3,21,276 kWh/Year

### 3.1.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 321276 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.1.4 Problem / Gap Identified

Without segregation and control refinement, the cooling system continues operating at higher condenser water temperatures and suboptimal flow conditions, increasing compressor and pump energy use.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.1.5 Proposed Project

1. VFD on dedicated CT Fan, 2. AI based Fan Speed Controller for all CT Fan 3. Dedicated Pump & Pipeline modification for Chiller Condenser Water with sensors & data display with cloud based data monitoring (Like BMS)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.1.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.1.7 Rationale for Energy Saving

Improved cooling tower segregation and condenser water control reduce heat rejection losses, improve chiller operating efficiency, and lower auxiliary pumping demand.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.1.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 32127.6 |
| Annual cost saving | ₹/year | 230354.892 |
| Estimated investment | ₹ | 350000 |
| Simple payback | years | 1.519394691 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.1.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 321276 |
| 2 | Energy saving | 32,128 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,30,355 |
| 5 | Estimated investment | ₹3,50,000 |
| 6 | Payback period | 1.52 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.1.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.1.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.1.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.1.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.1.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.1.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.1.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.1.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.1.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 32,128 kWh, resulting in annual cost saving of ₹2,30,355. With an estimated investment of ₹3,50,000, the simple payback period is expected to be 1.52 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.2 ECM 2 – Flow Optimization for CHW Secondary Pump

### 3.2.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Flow Optimization for CHW Secondary Pump |
| Project number | ECM 2 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Chilled Water Secondary Pump (2 Nos) |
| Existing operating condition | 1. Chilled water secondary pump no. 1 consumption is 73,488 kWh/Year 2. Chilled water secondary pump no. 2 consumption is 44,691 kWh/Year |
| Proposed intervention | AI based Pumps Flow Control for Chilled Water Secondary Pump with sensors (Delta T & Delta P) & data display with cloud based data monitoring (Like BMS) |
| Expected energy saving | 17,727 kWh/year |
| Expected annual cost saving | ₹1,27,102 |
| Estimated investment | ₹1,50,000 |
| Simple payback period | 1.18 years |
| Implementation duration | 8 to 10 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.2.2 Existing System Description

1. Chilled water secondary pump no. 1 consumption is 73,488 kWh/Year 
2. Chilled water secondary pump no. 2 consumption is 44,691 kWh/Year

### 3.2.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 118179 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.2.4 Problem / Gap Identified

The present operating approach results in avoidable energy losses or control inefficiencies during normal plant operation.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.2.5 Proposed Project

AI based Pumps Flow Control for Chilled Water Secondary Pump with sensors (Delta T & Delta P) & data display with cloud based data monitoring (Like BMS)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.2.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.2.7 Rationale for Energy Saving

The proposed intervention reduces avoidable losses and aligns energy consumption more closely with actual process demand.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.2.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 17726.85 |
| Annual cost saving | ₹/year | 127101.5145 |
| Estimated investment | ₹ | 150000 |
| Simple payback | years | 1.180159029 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.2.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 118179 |
| 2 | Energy saving | 17,727 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,27,102 |
| 5 | Estimated investment | ₹1,50,000 |
| 6 | Payback period | 1.18 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.2.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.2.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.2.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 8 to 10 weeks |
| Installation and commissioning | 8 to 10 weeks |

### 3.2.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.2.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.2.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.2.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.2.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.2.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 17,727 kWh, resulting in annual cost saving of ₹1,27,102. With an estimated investment of ₹1,50,000, the simple payback period is expected to be 1.18 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.3 ECM 3 – EE Improvement in Air Compressors & Pump Using CT Segregation

### 3.3.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | EE Improvement in Air Compressors & Pump Using CT Segregation |
| Project number | ECM 3 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | CT Water Secondary Pump (3 Nos) |
| Existing operating condition | 1. CT Seconadary Consumption (3 Nos) is 3,73,413 kWh/Year 2. LP Air Compressor Consumption is 13,74,572 kWh/Year 3. HP Air Compressor consumption is 15,65,920 kWh/Year |
| Proposed intervention | AI based Pumps Flow Control for CT Water Secondary Pump with sensors (Delta T & Delta P) & data display with cloud based data monitoring (Like BMS) |
| Expected energy saving | 1,44,227 kWh/year |
| Expected annual cost saving | ₹10,34,106 |
| Estimated investment | ₹4,50,000 |
| Simple payback period | 0.44 years |
| Implementation duration | 8 to 10 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.3.2 Existing System Description

1. CT Seconadary Consumption (3 Nos) is 3,73,413 kWh/Year
2. LP Air Compressor Consumption is 13,74,572 kWh/Year
3. HP Air Compressor consumption is 15,65,920 kWh/Year

### 3.3.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 3313905 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.3.4 Problem / Gap Identified

Without segregation and control refinement, the cooling system continues operating at higher condenser water temperatures and suboptimal flow conditions, increasing compressor and pump energy use.

| System | Typical Gap |
| --- | --- |
| Compressed air | Air leakage, pressure drops, inefficient generation |

### 3.3.5 Proposed Project

AI based Pumps Flow Control for CT Water Secondary Pump with sensors (Delta T & Delta P) & data display with cloud based data monitoring (Like BMS)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.3.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.3.7 Rationale for Energy Saving

Improved cooling tower segregation and condenser water control reduce heat rejection losses, improve chiller operating efficiency, and lower auxiliary pumping demand.

| Project Type | Saving Rationale |
| --- | --- |
| Compressed air | [To be updated after site data verification] |

### 3.3.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 144226.71 |
| Annual cost saving | ₹/year | 1034105.511 |
| Estimated investment | ₹ | 450000 |
| Simple payback | years | 0.4351586906 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.3.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 3313905 |
| 2 | Energy saving | 1,44,227 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹10,34,106 |
| 5 | Estimated investment | ₹4,50,000 |
| 6 | Payback period | 0.44 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.3.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.3.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.3.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 8 to 10 weeks |
| Installation and commissioning | 8 to 10 weeks |

### 3.3.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.3.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Pressure, flow, leakage, compressor kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.3.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.3.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.3.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.3.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 1,44,227 kWh, resulting in annual cost saving of ₹10,34,106. With an estimated investment of ₹4,50,000, the simple payback period is expected to be 0.44 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.4 ECM 4 – Automatic Primary Pump Flow Control for Chiller kW/TR Optimization

### 3.4.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization |
| Project number | ECM 4 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Chiller |
| Existing operating condition | 1. Chiller Consumption is 3,21,276 kWh/Year 2. Chilled water primary pump Consumption 63,000 kWh/Year |
| Proposed intervention | AI based Pumps Flow Control for Chiller Evaporator Water with sensors (Delta T & Delta P), Installation of VFD on chiller primary pump & data display with cloud based data monitoring (Like BMS) |
| Expected energy saving | 45,832 kWh/year |
| Expected annual cost saving | ₹3,28,615 |
| Estimated investment | ₹1,45,000 |
| Simple payback period | 0.44 years |
| Implementation duration | 8 to 10 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.4.2 Existing System Description

1. Chiller Consumption is 3,21,276 kWh/Year
2. Chilled water primary pump Consumption 63,000 kWh/Year

### 3.4.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 384276 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.4.4 Problem / Gap Identified

The present operating approach results in avoidable energy losses or control inefficiencies during normal plant operation.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.4.5 Proposed Project

AI based Pumps Flow Control for Chiller Evaporator Water with sensors (Delta T & Delta P), Installation of VFD on chiller primary pump & data display with cloud based data monitoring (Like BMS)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.4.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.4.7 Rationale for Energy Saving

The proposed intervention reduces avoidable losses and aligns energy consumption more closely with actual process demand.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.4.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 45831.9 |
| Annual cost saving | ₹/year | 328614.723 |
| Estimated investment | ₹ | 145000 |
| Simple payback | years | 0.4412462067 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.4.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 384276 |
| 2 | Energy saving | 45,832 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹3,28,615 |
| 5 | Estimated investment | ₹1,45,000 |
| 6 | Payback period | 0.44 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.4.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.4.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.4.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 8 to 10 weeks |
| Installation and commissioning | 8 to 10 weeks |

### 3.4.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.4.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.4.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.4.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.4.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.4.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 45,832 kWh, resulting in annual cost saving of ₹3,28,615. With an estimated investment of ₹1,45,000, the simple payback period is expected to be 0.44 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.5 ECM 5 – Free Cooling by Chiller Bypass in Winter

### 3.5.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Free Cooling by Chiller Bypass in Winter |
| Project number | ECM 5 |
| System | Utilty |
| Location | [To be updated after site data verification] |
| Equipment covered | Chiller |
| Existing operating condition | Chiller baseline consumption of month Nov, Dec & Jan is 62,146 kWh/year + Corresponding energy consumption in condenser pump & CT Fan (Evaporator Pump power will be required to circulate the water through PHE & CT). Existing decomissioned PHE at CT & Condenser water could be used. |
| Proposed intervention | Addional Pipe line from sump to the CT (dedicated for Chiller), Pump, Controls, Chiller auto ON/OFF, CT Water Pump auto ON/OFF (Central PLC & all sensors), Panel, Pipeline Modification, Using Existing PHE |
| Expected energy saving | 60,000 kWh/year |
| Expected annual cost saving | ₹4,30,200 |
| Estimated investment | ₹5,00,000 |
| Simple payback period | 1.16 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.5.2 Existing System Description

Chiller baseline consumption of month Nov, Dec & Jan is 62,146
kWh/year + Corresponding energy consumption in condenser pump & CT Fan (Evaporator Pump power will be required to circulate the water through PHE & CT). Existing decomissioned PHE at CT & Condenser water could be used.

### 3.5.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 100000 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.5.4 Problem / Gap Identified

Available ambient cooling potential is not fully utilized, so the chiller continues consuming power when free cooling could satisfy part of the thermal load.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.5.5 Proposed Project

Addional Pipe line from sump to the CT (dedicated for Chiller), Pump, Controls, Chiller auto ON/OFF, CT Water Pump auto ON/OFF (Central PLC & all sensors), Panel, Pipeline Modification, Using Existing PHE

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.5.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.5.7 Rationale for Energy Saving

Using ambient-assisted cooling during winter reduces compressor runtime while maintaining process cooling requirements.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.5.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 60000 |
| Annual cost saving | ₹/year | 430200 |
| Estimated investment | ₹ | 500000 |
| Simple payback | years | 1.162250116 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.5.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 100000 |
| 2 | Energy saving | 60,000 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹4,30,200 |
| 5 | Estimated investment | ₹5,00,000 |
| 6 | Payback period | 1.16 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.5.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.5.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.5.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.5.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.5.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.5.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.5.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.5.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.5.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 60,000 kWh, resulting in annual cost saving of ₹4,30,200. With an estimated investment of ₹5,00,000, the simple payback period is expected to be 1.16 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.6 ECM 8 – IE5 Efficiency Motor Retrofit for CHW Secondary Pump

### 3.6.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | IE5 Efficiency Motor Retrofit for CHW Secondary Pump |
| Project number | ECM 8 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Chilled Water Secondary Pump No. 3 |
| Existing operating condition | Measured power of chilled water secondary pump no. 3 is 20.33 kW |
| Proposed intervention | IE5 Efficiency Motor Retrofit for CHW Secondary Pump |
| Expected energy saving | 25,616 kWh/year |
| Expected annual cost saving | ₹1,83,665 |
| Estimated investment | ₹2,70,000 |
| Simple payback period | 1.47 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.6.2 Existing System Description

Measured power of chilled water secondary pump no. 3 is 20.33 kW

### 3.6.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 170772 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.6.4 Problem / Gap Identified

Motor losses and drive inefficiencies increase running energy consumption across the operating profile.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.6.5 Proposed Project

IE5 Efficiency Motor Retrofit for CHW Secondary Pump

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.6.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.6.7 Rationale for Energy Saving

Higher motor efficiency reduces electrical losses at the same load output and supports lower lifecycle energy cost.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.6.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 25615.8 |
| Annual cost saving | ₹/year | 183665.286 |
| Estimated investment | ₹ | 270000 |
| Simple payback | years | 1.470065497 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.6.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 170772 |
| 2 | Energy saving | 25,616 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,83,665 |
| 5 | Estimated investment | ₹2,70,000 |
| 6 | Payback period | 1.47 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.6.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.6.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.6.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.6.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.6.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.6.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.6.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.6.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.6.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 25,616 kWh, resulting in annual cost saving of ₹1,83,665. With an estimated investment of ₹2,70,000, the simple payback period is expected to be 1.47 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.7 ECM 9 – IE5 Efficiency Motor Retrofit for CT Water Secondary Pump

### 3.7.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump |
| Project number | ECM 9 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | CT Secondary Pump No. 1, 2 & 3 |
| Existing operating condition | 1. CT secondary pump no. 1 baseline consumption is 1,14,672 kWh/year 2. CT secondary pump no. 2 baseline consumption is 1,14,499 kWh/year 3. CT secondary pump no. 3 baseline consumption is 1,44,242 kWh/year |
| Proposed intervention | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump |
| Expected energy saving | 52,278 kWh/year |
| Expected annual cost saving | ₹3,74,832 |
| Estimated investment | ₹10,11,933 |
| Simple payback period | 2.7 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.7.2 Existing System Description

1. CT secondary pump no. 1 baseline consumption is 1,14,672 kWh/year
2. CT secondary pump no. 2 baseline consumption is 1,14,499  kWh/year
3. CT secondary pump no. 3 baseline consumption is 1,44,242   kWh/year

### 3.7.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 373413 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.7.4 Problem / Gap Identified

Motor losses and drive inefficiencies increase running energy consumption across the operating profile.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.7.5 Proposed Project

IE5 Efficiency Motor Retrofit for CT Water Secondary Pump

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.7.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.7.7 Rationale for Energy Saving

Higher motor efficiency reduces electrical losses at the same load output and supports lower lifecycle energy cost.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.7.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 52277.82 |
| Annual cost saving | ₹/year | 374831.9694 |
| Estimated investment | ₹ | 1011933 |
| Simple payback | years | 2.699697685 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.7.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 373413 |
| 2 | Energy saving | 52,278 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹3,74,832 |
| 5 | Estimated investment | ₹10,11,933 |
| 6 | Payback period | 2.7 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.7.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.7.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.7.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.7.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.7.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Flow, head, pressure, kW, CHW/CW temperature | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.7.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.7.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.7.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.7.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 52,278 kWh, resulting in annual cost saving of ₹3,74,832. With an estimated investment of ₹10,11,933, the simple payback period is expected to be 2.7 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

## GR-2 Production Machines

This section covers 8 energy conservation measures under the Production Machines category.

### Group Observation

### Implementation Focus

Implementation should combine site verification, detailed engineering, coordinated execution, and post-commissioning performance review.

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 13 | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers | ₹10,50,000 | ₹3,92,342 | 54720 | 2.67623382 |
| ECM 14 | Insulation hot flexible ducts (72 Nos) | ₹7,40,000 | ₹14,32,566 | 199800 | 0.5165556072 |
| ECM 15 | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) | ₹8,50,000 | ₹2,81,064 | 39200 | 3.024222241 |
| ECM 16 | ASB 70 DPH (7 Nos) Servo Motor Project | ₹52,50,000 | ₹19,39,535 | 270506.95 | 2.706834605 |
| ECM 17 | ASB 50 MB (18 Nos) Servo Motor Project | ₹90,00,000 | ₹30,55,386 | 426134.772 | 2.945617697 |
| ECM 18 | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project | ₹10,00,000 | ₹3,44,075 | 47988.15 | 2.906342794 |
| ECM 19 | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project | ₹6,00,000 | ₹2,01,857 | 28153.048 | 2.972396039 |
| ECM 20 | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project | ₹9,10,000 | ₹2,71,590 | 37878.6464 | 3.35064013 |

3.8 ECM 13 – Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers

### 3.8.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers |
| Project number | ECM 13 |
| System | ISBM |
| Location | [To be updated after site data verification] |
| Equipment covered | ASB 70 DPH (8) Dryer |
| Existing operating condition | 3.7 KW heater, drawing 3.8 KW, working hours 300 per year, 24 hrs/day |
| Proposed intervention | Recover Heat to Pre heat entering atmospheric air for regeneration heater on 1. B/ISBM/DPH/PPL2, 2. B/ISBM/DPH/06, 3. B/ISBM/DPH/02, 4. B/ISBM/DPH/03, 5. B/ISBM/DPH/05, 6. B/ISBM/DPH/PPL3, 7. B/ISBM/DPH/PPL4, 8. B/ISBM/DPH/P01 |
| Expected energy saving | 54,720 kWh/year |
| Expected annual cost saving | ₹3,92,342 |
| Estimated investment | ₹10,50,000 |
| Simple payback period | 2.68 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.8.2 Existing System Description

3.7 KW heater, drawing 3.8 KW, working hours 300 per year, 24 hrs/day

### 3.8.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 218880 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.8.4 Problem / Gap Identified

The present operating approach results in avoidable energy losses or control inefficiencies during normal plant operation.

| System | Typical Gap |
| --- | --- |
| Heat recovery | Waste heat discharged without useful recovery |

### 3.8.5 Proposed Project

Recover Heat to Pre heat entering atmospheric air for regeneration heater on 1. B/ISBM/DPH/PPL2, 2. B/ISBM/DPH/06, 3. B/ISBM/DPH/02, 4. B/ISBM/DPH/03, 5. B/ISBM/DPH/05, 6. B/ISBM/DPH/PPL3, 7. B/ISBM/DPH/PPL4, 8. B/ISBM/DPH/P01

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.8.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.8.7 Rationale for Energy Saving

The proposed intervention reduces avoidable losses and aligns energy consumption more closely with actual process demand.

| Project Type | Saving Rationale |
| --- | --- |
| Heat recovery | [To be updated after site data verification] |

### 3.8.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 54720 |
| Annual cost saving | ₹/year | 392342.4 |
| Estimated investment | ₹ | 1050000 |
| Simple payback | years | 2.67623382 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.8.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 218880 |
| 2 | Energy saving | 54,720 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹3,92,342 |
| 5 | Estimated investment | ₹10,50,000 |
| 6 | Payback period | 2.68 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.8.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.8.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.8.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.8.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.8.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Exhaust air temperature, inlet air temperature, heater kW, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.8.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.8.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.8.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.8.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 54,720 kWh, resulting in annual cost saving of ₹3,92,342. With an estimated investment of ₹10,50,000, the simple payback period is expected to be 2.68 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.9 ECM 14 – Insulation hot flexible ducts (72 Nos)

### 3.9.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Insulation hot flexible ducts (72 Nos) |
| Project number | ECM 14 |
| System | ISBM |
| Location | [To be updated after site data verification] |
| Equipment covered | ASB 70 DPH (11), 12M (8), 50 MB (18) : 2 ducts per machine |
| Existing operating condition | 0.75 KW/machine loss prevention, working hours 300 per year, 24 hrs/day |
| Proposed intervention | Insulating hot ducts for machines: ASB 70 DPH (11 Nos.), 12M (8 Nos.), 50 MB (18 Nos.): 2 ducts per machine (total: 37 machines, 74 Ducts) |
| Expected energy saving | 1,99,800 kWh/year |
| Expected annual cost saving | ₹14,32,566 |
| Estimated investment | ₹7,40,000 |
| Simple payback period | 0.52 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.9.2 Existing System Description

0.75 KW/machine loss prevention, working hours 300 per year, 24 hrs/day

### 3.9.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 299700 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.9.4 Problem / Gap Identified

Uninsulated or poorly insulated hot ducts lose useful heat before it reaches the process, increasing electrical heating consumption.

| System | Typical Gap |
| --- | --- |
| Insulation | Heat loss from exposed hot surfaces or ducts |

### 3.9.5 Proposed Project

Insulating hot ducts for machines: ASB 70 DPH (11 Nos.), 12M (8 Nos.), 50 MB (18 Nos.): 2 ducts per machine (total: 37 machines, 74 Ducts)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.9.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.9.7 Rationale for Energy Saving

Lower thermal losses reduce heater energy input while improving temperature retention and process stability.

| Project Type | Saving Rationale |
| --- | --- |
| Insulation | [To be updated after site data verification] |

### 3.9.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 199800 |
| Annual cost saving | ₹/year | 1432566 |
| Estimated investment | ₹ | 740000 |
| Simple payback | years | 0.5165556072 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.9.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 299700 |
| 2 | Energy saving | 1,99,800 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹14,32,566 |
| 5 | Estimated investment | ₹7,40,000 |
| 6 | Payback period | 0.52 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.9.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.9.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.9.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.9.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.9.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Surface temperature, duct temperature, heater load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.9.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.9.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.9.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.9.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 1,99,800 kWh, resulting in annual cost saving of ₹14,32,566. With an estimated investment of ₹7,40,000, the simple payback period is expected to be 0.52 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.10 ECM 15 – Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos)

### 3.10.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) |
| Project number | ECM 15 |
| System | ISBM |
| Location | [To be updated after site data verification] |
| Equipment covered | ASB 70 DPH (8) Machine |
| Existing operating condition | The existing system operates under current process conditions but exhibits opportunities for measurable energy-performance improvement. |
| Proposed intervention | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) |
| Expected energy saving | 39,200 kWh/year |
| Expected annual cost saving | ₹2,81,064 |
| Estimated investment | ₹8,50,000 |
| Simple payback period | 3.02 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.10.2 Existing System Description

The existing system operates under current process conditions but exhibits opportunities for measurable energy-performance improvement.

### 3.10.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 112000 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.10.4 Problem / Gap Identified

The present operating approach results in avoidable energy losses or control inefficiencies during normal plant operation.

| System | Typical Gap |
| --- | --- |
| Insulation | Heat loss from exposed hot surfaces or ducts |

### 3.10.5 Proposed Project

Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos)

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.10.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.10.7 Rationale for Energy Saving

1. load Comming On pump due to lubricatoin problem.                                                                                                       2. Energy losses due to  contineus water pump running.                                                                                                              3. energy loss due to operation air waste.

| Project Type | Saving Rationale |
| --- | --- |
| Insulation | [To be updated after site data verification] |

### 3.10.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 39200 |
| Annual cost saving | ₹/year | 281064 |
| Estimated investment | ₹ | 850000 |
| Simple payback | years | 3.024222241 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.10.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 112000 |
| 2 | Energy saving | 39,200 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,81,064 |
| 5 | Estimated investment | ₹8,50,000 |
| 6 | Payback period | 3.02 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.10.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.10.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.10.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.10.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.10.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Surface temperature, duct temperature, heater load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.10.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.10.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.10.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.10.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 39,200 kWh, resulting in annual cost saving of ₹2,81,064. With an estimated investment of ₹8,50,000, the simple payback period is expected to be 3.02 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.11 ECM 16 – ASB 70 DPH (7 Nos) Servo Motor Project

### 3.11.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | ASB 70 DPH (7 Nos) Servo Motor Project |
| Project number | ECM 16 |
| System | ISBM |
| Location | [To be updated after site data verification] |
| Equipment covered | ASB 70 DPH (7) Machines |
| Existing operating condition | The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions. |
| Proposed intervention | ASB 70 DPH (7 Nos) Servo Motor Project |
| Expected energy saving | 2,70,507 kWh/year |
| Expected annual cost saving | ₹19,39,535 |
| Estimated investment | ₹52,50,000 |
| Simple payback period | 2.71 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.11.2 Existing System Description

The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions.

### 3.11.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 772877 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.11.4 Problem / Gap Identified

Conventional drive operation causes excess energy consumption during idle and low-load periods while limiting process-response precision.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.11.5 Proposed Project

ASB 70 DPH (7 Nos) Servo Motor Project

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.11.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.11.7 Rationale for Energy Saving

Servo drive control better matches output to process demand, reducing motor losses, hydraulic throttling, and idle energy draw.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.11.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 270506.95 |
| Annual cost saving | ₹/year | 1939534.832 |
| Estimated investment | ₹ | 5250000 |
| Simple payback | years | 2.706834605 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.11.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 772877 |
| 2 | Energy saving | 2,70,507 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹19,39,535 |
| 5 | Estimated investment | ₹52,50,000 |
| 6 | Payback period | 2.71 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.11.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.11.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.11.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.11.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.11.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.11.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.11.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.11.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.11.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 2,70,507 kWh, resulting in annual cost saving of ₹19,39,535. With an estimated investment of ₹52,50,000, the simple payback period is expected to be 2.71 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.12 ECM 17 – ASB 50 MB (18 Nos) Servo Motor Project

### 3.12.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | ASB 50 MB (18 Nos) Servo Motor Project |
| Project number | ECM 17 |
| System | ISBM |
| Location | [To be updated after site data verification] |
| Equipment covered | ASB 50MB (18 Machines) |
| Existing operating condition | 67640.44 |
| Proposed intervention | ASB 50 MB (18 Nos) Servo Motor Project |
| Expected energy saving | 4,26,135 kWh/year |
| Expected annual cost saving | ₹30,55,386 |
| Estimated investment | ₹90,00,000 |
| Simple payback period | 2.95 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.12.2 Existing System Description

67640.44

### 3.12.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 1217527.92 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.12.4 Problem / Gap Identified

Conventional drive operation causes excess energy consumption during idle and low-load periods while limiting process-response precision.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.12.5 Proposed Project

ASB 50 MB (18 Nos) Servo Motor Project

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.12.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.12.7 Rationale for Energy Saving

Servo drive control better matches output to process demand, reducing motor losses, hydraulic throttling, and idle energy draw.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.12.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 426134.772 |
| Annual cost saving | ₹/year | 3055386.315 |
| Estimated investment | ₹ | 9000000 |
| Simple payback | years | 2.945617697 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.12.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 1217527.92 |
| 2 | Energy saving | 4,26,135 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹30,55,386 |
| 5 | Estimated investment | ₹90,00,000 |
| 6 | Payback period | 2.95 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.12.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.12.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.12.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.12.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.12.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.12.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.12.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.12.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.12.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 4,26,135 kWh, resulting in annual cost saving of ₹30,55,386. With an estimated investment of ₹90,00,000, the simple payback period is expected to be 2.95 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.13 ECM 18 – EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project

### 3.13.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project |
| Project number | ECM 18 |
| System | EBM |
| Location | [To be updated after site data verification] |
| Equipment covered | EBM CMP Old Machines (5 Nos) |
| Existing operating condition | The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions. |
| Proposed intervention | Replace Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B/EBM/23, 2. B/EBM/39, 3. B/EBM/40, 4. B/EBM/41, 5. B/EBM/42. These are 7.5 kW Induction Hydraullic Motors. |
| Expected energy saving | 47,988 kWh/year |
| Expected annual cost saving | ₹3,44,075 |
| Estimated investment | ₹10,00,000 |
| Simple payback period | 2.91 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.13.2 Existing System Description

The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions.

### 3.13.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 137109 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.13.4 Problem / Gap Identified

Conventional drive operation causes excess energy consumption during idle and low-load periods while limiting process-response precision.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.13.5 Proposed Project

Replace  Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B/EBM/23, 2. B/EBM/39, 3. B/EBM/40, 4. B/EBM/41, 5. B/EBM/42. These are 7.5 kW Induction Hydraullic Motors.

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.13.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.13.7 Rationale for Energy Saving

Servo drive control better matches output to process demand, reducing motor losses, hydraulic throttling, and idle energy draw.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.13.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 47988.15 |
| Annual cost saving | ₹/year | 344075.0355 |
| Estimated investment | ₹ | 1000000 |
| Simple payback | years | 2.906342794 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.13.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 137109 |
| 2 | Energy saving | 47,988 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹3,44,075 |
| 5 | Estimated investment | ₹10,00,000 |
| 6 | Payback period | 2.91 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.13.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.13.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.13.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.13.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.13.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.13.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.13.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.13.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.13.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 47,988 kWh, resulting in annual cost saving of ₹3,44,075. With an estimated investment of ₹10,00,000, the simple payback period is expected to be 2.91 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.14 ECM 19 – EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project

### 3.14.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project |
| Project number | ECM 19 |
| System | EBM |
| Location | [To be updated after site data verification] |
| Equipment covered | EBM CMP Old Machines |
| Existing operating condition | The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions. |
| Proposed intervention | Replace Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B/EBM/28, 2. B/EBM/29, 3. B/EBM/30, 4.B/EBM/31 in this machine 5.5 kW Induction Hydraullic Motor is present |
| Expected energy saving | 28,153 kWh/year |
| Expected annual cost saving | ₹2,01,857 |
| Estimated investment | ₹6,00,000 |
| Simple payback period | 2.97 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.14.2 Existing System Description

The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions.

### 3.14.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 80437.28 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.14.4 Problem / Gap Identified

Conventional drive operation causes excess energy consumption during idle and low-load periods while limiting process-response precision.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.14.5 Proposed Project

Replace  Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B/EBM/28, 2. B/EBM/29, 3. B/EBM/30, 4.B/EBM/31  in this machine 5.5 kW Induction Hydraullic Motor is present

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.14.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.14.7 Rationale for Energy Saving

Servo drive control better matches output to process demand, reducing motor losses, hydraulic throttling, and idle energy draw.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.14.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 28153.048 |
| Annual cost saving | ₹/year | 201857.3542 |
| Estimated investment | ₹ | 600000 |
| Simple payback | years | 2.972396039 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.14.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 80437.28 |
| 2 | Energy saving | 28,153 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,01,857 |
| 5 | Estimated investment | ₹6,00,000 |
| 6 | Payback period | 2.97 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.14.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.14.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.14.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.14.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.14.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.14.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.14.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.14.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.14.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 28,153 kWh, resulting in annual cost saving of ₹2,01,857. With an estimated investment of ₹6,00,000, the simple payback period is expected to be 2.97 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.15 ECM 20 – EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project

### 3.15.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project |
| Project number | ECM 20 |
| System | EBM |
| Location | [To be updated after site data verification] |
| Equipment covered | EBM CMP Old Machines |
| Existing operating condition | The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions. |
| Proposed intervention | Replace Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B1/EBM/08, 2. B1/EBM/10, 3. B1/EBM/11, 4. B/EBM/14, 5. B/EBM/18, 6. B/EBM/21, 7. B/EBM/22 in this machine 3.7 kW Induction Hydraullic Motor is present |
| Expected energy saving | 37,879 kWh/year |
| Expected annual cost saving | ₹2,71,590 |
| Estimated investment | ₹9,10,000 |
| Simple payback period | 3.35 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.15.2 Existing System Description

The existing machine drive arrangement relies on conventional motor-hydraulic operation with avoidable idle losses and reduced controllability during part-load conditions.

### 3.15.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 94696.616 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.15.4 Problem / Gap Identified

Conventional drive operation causes excess energy consumption during idle and low-load periods while limiting process-response precision.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.15.5 Proposed Project

Replace  Induction Hydraulic Motor with Servo Hydraulic Motor in 1. B1/EBM/08, 2. B1/EBM/10, 3. B1/EBM/11, 4. B/EBM/14, 5. B/EBM/18, 6. B/EBM/21, 7. B/EBM/22 in this machine 3.7 kW Induction Hydraullic Motor is present

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.15.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.15.7 Rationale for Energy Saving

Servo drive control better matches output to process demand, reducing motor losses, hydraulic throttling, and idle energy draw.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.15.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 37878.6464 |
| Annual cost saving | ₹/year | 271589.8947 |
| Estimated investment | ₹ | 910000 |
| Simple payback | years | 3.35064013 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.15.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 94696.616 |
| 2 | Energy saving | 37,879 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,71,590 |
| 5 | Estimated investment | ₹9,10,000 |
| 6 | Payback period | 3.35 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.15.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.15.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.15.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.15.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.15.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Hydraulic motor kW, cycle time, idle load, operating hours | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.15.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.15.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.15.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.15.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 37,879 kWh, resulting in annual cost saving of ₹2,71,590. With an estimated investment of ₹9,10,000, the simple payback period is expected to be 3.35 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

## GR-3 Air Compressors

This section covers 2 energy conservation measures under the Air Compressors category.

### Group Observation

### Implementation Focus

Implementation should combine site verification, detailed engineering, coordinated execution, and post-commissioning performance review.

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 21 | Compressed Air Measurement & Management | ₹8,00,000 | ₹10,54,166 | 147024.6 | 0.7588934856 |
| ECM 22 | Booster Compressor retrofit with IE5 Efficiency motor & automation | ₹2,58,868 | ₹1,05,299 | 14686 | 2.458414935 |

3.16 ECM 21 – Compressed Air Measurement & Management

### 3.16.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Compressed Air Measurement & Management |
| Project number | ECM 21 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Air Compressors (4 Nos: 1 LP, 3 HP) |
| Existing operating condition | 1. LP Air Compressor Consumption is 13,74,572 kWh/Year, 2. HP Air Compressor consumption is 15,65,920 kWh/Year |
| Proposed intervention | Compressed Air Measurement & Management |
| Expected energy saving | 1,47,025 kWh/year |
| Expected annual cost saving | ₹10,54,166 |
| Estimated investment | ₹8,00,000 |
| Simple payback period | 0.76 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | I |

### 3.16.2 Existing System Description

1. LP Air Compressor Consumption is 13,74,572 kWh/Year, 2. HP Air Compressor consumption is 15,65,920 kWh/Year

### 3.16.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 2940492 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.16.4 Problem / Gap Identified

Insufficient system measurement and control can increase specific power consumption, leakage losses, and unloaded compressor operation.

| System | Typical Gap |
| --- | --- |
| Compressed air | Air leakage, pressure drops, inefficient generation |

### 3.16.5 Proposed Project

Compressed Air Measurement & Management

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.16.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.16.7 Rationale for Energy Saving

Better compressor efficiency and air-demand management reduce specific energy consumption while maintaining required pressure and flow reliability.

| Project Type | Saving Rationale |
| --- | --- |
| Compressed air | [To be updated after site data verification] |

### 3.16.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 147024.6 |
| Annual cost saving | ₹/year | 1054166.382 |
| Estimated investment | ₹ | 800000 |
| Simple payback | years | 0.7588934856 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.16.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 2940492 |
| 2 | Energy saving | 1,47,025 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹10,54,166 |
| 5 | Estimated investment | ₹8,00,000 |
| 6 | Payback period | 0.76 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.16.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.16.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.16.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.16.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.16.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Pressure, flow, leakage, compressor kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.16.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.16.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.16.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.16.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 1,47,025 kWh, resulting in annual cost saving of ₹10,54,166. With an estimated investment of ₹8,00,000, the simple payback period is expected to be 0.76 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under I.

3.17 ECM 22 – Booster Compressor retrofit with IE5 Efficiency motor & automation

### 3.17.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Booster Compressor retrofit with IE5 Efficiency motor & automation |
| Project number | ECM 22 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | HP Booster Compressor |
| Existing operating condition | IE5 Motor with VFD and PID automation using pressure transmitter |
| Proposed intervention | Booster Compressor retrofit with IE5 Efficiency motor & automation |
| Expected energy saving | 14,686 kWh/year |
| Expected annual cost saving | ₹1,05,299 |
| Estimated investment | ₹2,58,868 |
| Simple payback period | 2.46 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.17.2 Existing System Description

IE5 Motor with VFD and PID automation using pressure transmitter

### 3.17.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 41960 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.17.4 Problem / Gap Identified

Insufficient system measurement and control can increase specific power consumption, leakage losses, and unloaded compressor operation.

| System | Typical Gap |
| --- | --- |
| Compressed air | Air leakage, pressure drops, inefficient generation |

### 3.17.5 Proposed Project

Booster Compressor retrofit with IE5 Efficiency motor & automation

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.17.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.17.7 Rationale for Energy Saving

Better compressor efficiency and air-demand management reduce specific energy consumption while maintaining required pressure and flow reliability.

| Project Type | Saving Rationale |
| --- | --- |
| Compressed air | [To be updated after site data verification] |

### 3.17.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 14686 |
| Annual cost saving | ₹/year | 105298.62 |
| Estimated investment | ₹ | 258867.7 |
| Simple payback | years | 2.458414935 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.17.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 41960 |
| 2 | Energy saving | 14,686 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,05,299 |
| 5 | Estimated investment | ₹2,58,868 |
| 6 | Payback period | 2.46 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.17.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.17.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.17.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.17.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.17.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Pressure, flow, leakage, compressor kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.17.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.17.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.17.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.17.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 14,686 kWh, resulting in annual cost saving of ₹1,05,299. With an estimated investment of ₹2,58,868, the simple payback period is expected to be 2.46 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

## GR-4 Auxiliary Systems & Machine Improvement

This section covers 5 energy conservation measures under the Auxiliary Systems & Machine Improvement category.

### Group Observation

### Implementation Focus

Implementation should combine site verification, detailed engineering, coordinated execution, and post-commissioning performance review.

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 6 | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit | ₹4,88,750 | ₹1,76,561 | 24624.9 | 2.768172432 |
| ECM 7 | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans | ₹3,10,000 | ₹1,40,543 | 19601.6 | 2.205723223 |
| ECM 10 | Cutting Grinders Retrofit with IE5 Motor & Cogged belt | ₹4,88,599 | ₹2,00,760 | 28000 | 2.433745517 |
| ECM 11 | PD blower Direct Mounting with IE5 motor with existing VFD | ₹2,70,000 | ₹1,24,220 | 17325 | 2.173558659 |
| ECM 12 | APFC relay for 600 kVAr Panel | ₹50,000 | ₹12,11,273 | 168936.3 | 0.0412788767 |

3.18 ECM 6 – CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit

### 3.18.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit |
| Project number | ECM 6 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | Cooling Tower Fan Motor, Its Mounting & Blades |
| Existing operating condition | CT No.2 baseline consumption is 54,772 kWh/Year |
| Proposed intervention | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit |
| Expected energy saving | 24,625 kWh/year |
| Expected annual cost saving | ₹1,76,561 |
| Estimated investment | ₹4,88,750 |
| Simple payback period | 2.77 years |
| Implementation duration | 12 to 14 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.18.2 Existing System Description

CT No.2 baseline consumption is 54,772 kWh/Year

### 3.18.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 54722 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.18.4 Problem / Gap Identified

Motor losses and drive inefficiencies increase running energy consumption across the operating profile.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.18.5 Proposed Project

CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.18.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.18.7 Rationale for Energy Saving

Higher motor efficiency reduces electrical losses at the same load output and supports lower lifecycle energy cost.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.18.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 24624.9 |
| Annual cost saving | ₹/year | 176560.533 |
| Estimated investment | ₹ | 488750 |
| Simple payback | years | 2.768172432 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.18.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 54722 |
| 2 | Energy saving | 24,625 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,76,561 |
| 5 | Estimated investment | ₹4,88,750 |
| 6 | Payback period | 2.77 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.18.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.18.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.18.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 12 to 14 weeks |
| Installation and commissioning | 12 to 14 weeks |

### 3.18.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.18.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.18.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.18.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.18.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.18.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 24,625 kWh, resulting in annual cost saving of ₹1,76,561. With an estimated investment of ₹4,88,750, the simple payback period is expected to be 2.77 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.19 ECM 7 – Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans

### 3.19.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans |
| Project number | ECM 7 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | AHUs (Blower + Motor Change) |
| Existing operating condition | 1. Clean Room pharma AHU baseline consumption is 30,776 kWh/year. 2. IM 2nd floor AHU baseline consumption is 18228 kWh/year. |
| Proposed intervention | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans |
| Expected energy saving | 19,602 kWh/year |
| Expected annual cost saving | ₹1,40,543 |
| Estimated investment | ₹3,10,000 |
| Simple payback period | 2.21 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.19.2 Existing System Description

1. Clean Room pharma AHU baseline consumption is 30,776 kWh/year.
2. IM 2nd floor AHU baseline consumption is 18228 kWh/year.

### 3.19.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 49004 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.19.4 Problem / Gap Identified

The present operating approach results in avoidable energy losses or control inefficiencies during normal plant operation.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.19.5 Proposed Project

Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.19.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.19.7 Rationale for Energy Saving

The proposed intervention reduces avoidable losses and aligns energy consumption more closely with actual process demand.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.19.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 19601.6 |
| Annual cost saving | ₹/year | 140543.472 |
| Estimated investment | ₹ | 310000 |
| Simple payback | years | 2.205723223 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.19.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 49004 |
| 2 | Energy saving | 19,602 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,40,543 |
| 5 | Estimated investment | ₹3,10,000 |
| 6 | Payback period | 2.21 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.19.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.19.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.19.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.19.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.19.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | Airflow, static pressure, fan kW | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.19.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.19.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.19.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.19.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 19,602 kWh, resulting in annual cost saving of ₹1,40,543. With an estimated investment of ₹3,10,000, the simple payback period is expected to be 2.21 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.20 ECM 10 – Cutting Grinders Retrofit with IE5 Motor & Cogged belt

### 3.20.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | Cutting Grinders Retrofit with IE5 Motor & Cogged belt |
| Project number | ECM 10 |
| System | Process |
| Location | [To be updated after site data verification] |
| Equipment covered | Cutting Grinders |
| Existing operating condition | The existing motor-driven system operates with standard-efficiency equipment and associated losses that are higher than currently available premium-efficiency alternatives. |
| Proposed intervention | Cutting Grinders Retrofit with IE5 Motor & Cogged belt |
| Expected energy saving | 28,000 kWh/year |
| Expected annual cost saving | ₹2,00,760 |
| Estimated investment | ₹4,88,599 |
| Simple payback period | 2.43 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.20.2 Existing System Description

The existing motor-driven system operates with standard-efficiency equipment and associated losses that are higher than currently available premium-efficiency alternatives.

### 3.20.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 140000 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.20.4 Problem / Gap Identified

Motor losses and drive inefficiencies increase running energy consumption across the operating profile.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.20.5 Proposed Project

Cutting Grinders Retrofit with IE5 Motor & Cogged belt

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.20.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.20.7 Rationale for Energy Saving

Higher motor efficiency reduces electrical losses at the same load output and supports lower lifecycle energy cost.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.20.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 28000 |
| Annual cost saving | ₹/year | 200760 |
| Estimated investment | ₹ | 488598.75 |
| Simple payback | years | 2.433745517 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.20.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 140000 |
| 2 | Energy saving | 28,000 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹2,00,760 |
| 5 | Estimated investment | ₹4,88,599 |
| 6 | Payback period | 2.43 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.20.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.20.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.20.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.20.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.20.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.20.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.20.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.20.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.20.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 28,000 kWh, resulting in annual cost saving of ₹2,00,760. With an estimated investment of ₹4,88,599, the simple payback period is expected to be 2.43 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.21 ECM 11 – PD blower Direct Mounting with IE5 motor with existing VFD

### 3.21.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | PD blower Direct Mounting with IE5 motor with existing VFD |
| Project number | ECM 11 |
| System | Process |
| Location | [To be updated after site data verification] |
| Equipment covered | PD Blower |
| Existing operating condition | The existing motor-driven system operates with standard-efficiency equipment and associated losses that are higher than currently available premium-efficiency alternatives. |
| Proposed intervention | PD blower Direct Mounting with IE5 motor with existing VFD |
| Expected energy saving | 17,325 kWh/year |
| Expected annual cost saving | ₹1,24,220 |
| Estimated investment | ₹2,70,000 |
| Simple payback period | 2.17 years |
| Implementation duration | 10 to 12 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.21.2 Existing System Description

The existing motor-driven system operates with standard-efficiency equipment and associated losses that are higher than currently available premium-efficiency alternatives.

### 3.21.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 57750 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.21.4 Problem / Gap Identified

Motor losses and drive inefficiencies increase running energy consumption across the operating profile.

| System | Typical Gap |
| --- | --- |
| System | [To be updated after site data verification] |

### 3.21.5 Proposed Project

PD blower Direct Mounting with IE5 motor with existing VFD

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.21.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.21.7 Rationale for Energy Saving

Higher motor efficiency reduces electrical losses at the same load output and supports lower lifecycle energy cost.

| Project Type | Saving Rationale |
| --- | --- |
| Project | [To be updated after site data verification] |

### 3.21.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 17325 |
| Annual cost saving | ₹/year | 124220.25 |
| Estimated investment | ₹ | 270000 |
| Simple payback | years | 2.173558659 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.21.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 57750 |
| 2 | Energy saving | 17,325 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹1,24,220 |
| 5 | Estimated investment | ₹2,70,000 |
| 6 | Payback period | 2.17 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.21.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.21.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.21.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 10 to 12 weeks |
| Installation and commissioning | 10 to 12 weeks |

### 3.21.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.21.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | ECM-type-specific parameter | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.21.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.21.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.21.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.21.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 17,325 kWh, resulting in annual cost saving of ₹1,24,220. With an estimated investment of ₹2,70,000, the simple payback period is expected to be 2.17 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

3.22 ECM 12 – APFC relay for 600 kVAr Panel

### 3.22.1 Project Summary

| Particular | Details |
| --- | --- |
| Project title | APFC relay for 600 kVAr Panel |
| Project number | ECM 12 |
| System | Utility |
| Location | [To be updated after site data verification] |
| Equipment covered | APFC |
| Existing operating condition | Total KVAH incremental loss (As compared to KWH) in past 4 months projected on one year |
| Proposed intervention | APFC relay for 600 kVAr Panel |
| Expected energy saving | 1,68,936 kWh/year |
| Expected annual cost saving | ₹12,11,273 |
| Estimated investment | ₹50,000 |
| Simple payback period | 0.04 years |
| Implementation duration | 2 to 3 weeks |
| Implementation priority | [To be updated after site data verification] |

### 3.22.2 Existing System Description

Total KVAH incremental loss (As compared to KWH) in past 4 months projected on one year

### 3.22.3 Baseline Data and Measurements

| Parameter | Unit | Value |
| --- | --- | --- |
| Equipment rating | kW / TR / HP | [To be updated after site data verification] |
| Quantity | Nos. | [To be updated after site data verification] |
| Operating hours | hours/day | [To be updated after site data verification] |
| Operating days | days/year | [To be updated after site data verification] |
| Existing power consumption | kW | [To be updated after site data verification] |
| Annual operating hours | hours/year | [To be updated after site data verification] |
| Baseline annual consumption | kWh/year | 187707 |
| Average tariff | ₹/kWh | [To be updated after site data verification] |
| Baseline annual energy cost | ₹/year | [To be updated after site data verification] |

| Measurement | Unit | Value |
| --- | --- | --- |
| Voltage | V | [To be updated after site data verification] |
| Current | A | [To be updated after site data verification] |
| Power factor | - | [To be updated after site data verification] |
| Measured power | kW | [To be updated after site data verification] |
| Flow / airflow | m3/hr / CFM | [To be updated after site data verification] |
| Pressure / head / static pressure | m / mmWC / bar | [To be updated after site data verification] |
| Temperature inlet | °C | [To be updated after site data verification] |
| Temperature outlet | °C | [To be updated after site data verification] |
| Operating frequency | Hz | [To be updated after site data verification] |

### 3.22.4 Problem / Gap Identified

Suboptimal APFC operation can increase reactive power draw, reduce power factor, and expose the facility to avoidable demand-related penalties or inefficiencies.

| System | Typical Gap |
| --- | --- |
| APFC | Low PF or kVAh billing loss |

### 3.22.5 Proposed Project

APFC relay for 600 kVAr Panel

| Sr. No. | Scope Item |
| --- | --- |
| 1 | Detailed site measurement and final engineering |
| 2 | Supply of equipment / VFD / controller / motor / sensor / panel as applicable |
| 3 | Installation and integration with existing system |
| 4 | Cabling, piping or ducting modification, if required |
| 5 | Testing and commissioning |
| 6 | Performance monitoring |
| 7 | Operator training and handover |

### 3.22.6 Key Activities for Implementation

| Activity | Details | Responsibility |
| --- | --- | --- |
| Site verification | Confirm equipment rating, location and operating condition | SEE-Tech + Client |
| Design finalization | Finalize technical specifications and control logic | SEE-Tech |
| Procurement | Arrange equipment and accessories | SEE-Tech / Vendor |
| Installation | Install system with minimum disturbance | SEE-Tech / Vendor |
| Integration | Integrate with panel / BMS / controls | SEE-Tech |
| Trial run | Operate under different load conditions | SEE-Tech + Client |
| Measurement | Record before and after performance | SEE-Tech |
| Handover | Submit performance report and train operators | SEE-Tech |

### 3.22.7 Rationale for Energy Saving

Improved reactive power management reduces avoidable electrical losses and supports stronger utilization of the connected electrical infrastructure.

| Project Type | Saving Rationale |
| --- | --- |
| APFC | [To be updated after site data verification] |

### 3.22.8 Energy Saving Calculation

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 168936.3 |
| Annual cost saving | ₹/year | 1211273.271 |
| Estimated investment | ₹ | 50000 |
| Simple payback | years | 0.0412788767 |

Annual Energy Saving = Load Reduction × Annual Operating Hours | Annual Cost Saving = Annual Energy Saving × Average Electricity Tariff | Simple Payback = Estimated Investment / Annual Cost Saving

### 3.22.9 Key Metrics

| Sr. No. | Parameter | Value |
| --- | --- | --- |
| 1 | Baseline consumption | 187707 |
| 2 | Energy saving | 1,68,936 kWh/year |
| 3 | Percentage saving | [Calculation pending] |
| 4 | Cost saving | ₹12,11,273 |
| 5 | Estimated investment | ₹50,000 |
| 6 | Payback period | 0.04 years |
| 7 | CO2 reduction | [Calculation pending] |

### 3.22.10 Technical Specifications

| Item | Specification |
| --- | --- |
| Equipment / technology | [To be updated after site data verification] |
| Capacity | [To be updated after site data verification] |
| Quantity | [To be updated after site data verification] |
| Motor efficiency class, if applicable | [To be updated after site data verification] |
| VFD rating, if applicable | [To be updated after site data verification] |
| Sensor type | [To be updated after site data verification] |
| Controller / PLC / IoT system | [To be updated after site data verification] |
| Communication | [To be updated after site data verification] |
| Panel requirement | [To be updated after site data verification] |
| Civil / mechanical modification | [To be updated after site data verification] |
| Safety requirement | [To be updated after site data verification] |

### 3.22.11 Schematic / Conceptual Framework

| Stage | Description |
| --- | --- |
| Stage 1: Current State | Existing inefficient or non-optimized operation |
| Stage 2: Intervention | What SEE-Tech will install or modify |
| Stage 3: Physics of Saving | Why energy will reduce after the intervention |
| Stage 4: Outcome | kWh saving, ₹ saving, payback and reliability benefit |

[Schematic / conceptual diagram to be inserted after engineering finalization]

### 3.22.12 Implementation Duration

| Activity | Duration |
| --- | --- |
| Engineering and procurement | 2 to 3 weeks |
| Installation and commissioning | 2 to 3 weeks |

### 3.22.13 Precautions / Aspects to be Taken Care Of

| Area | Precaution |
| --- | --- |
| Technical suitability | Confirm equipment rating, sizing and compatibility |
| Operation | Ensure project does not affect comfort, safety or process requirement |
| Controls | Test control logic under different load conditions |
| Electrical safety | Ensure proper protection, earthing and panel safety |
| Maintenance | Train maintenance team for operation and troubleshooting |
| Measurement | Record before and after data for savings validation |
| Shutdown planning | Plan installation during low-load or non-operating hours |

### 3.22.14 Measurement and Verification Plan

| Parameter | Baseline Measurement | Post-Implementation Measurement |
| --- | --- | --- |
| Power consumption | kW before project | kW after project |
| Operating hours | Existing operating schedule | Revised operating schedule |
| Energy consumption | kWh/year baseline | kWh/year after project |
| Performance parameter | PF, kVA, kVAh, reactive power compensation | Confirmed after commissioning |
| Saving validation | Calculated from baseline | Verified from measured data |

Savings shall be validated by measuring the power consumption and operating pattern before and after implementation. The final saving will be calculated based on measured load reduction, actual operating hours and applicable electricity tariff.

### 3.22.15 Benefits Other Than Energy Saving

| Benefit | Description |
| --- | --- |
| Reduced operating cost | Lower electricity / fuel bill |
| Improved reliability | Better control and reduced stress on equipment |
| Better comfort / process stability | Stable process operation, comfort or utility performance |
| Lower maintenance | Reduced wear and tear |
| Better monitoring | Availability of performance data where monitoring is included |
| Sustainability | Reduction in CO2 emissions after verified saving |
| Modernization | Upgrade of old system with efficient technology |

### 3.22.16 Carbon Footprint Reduction

[Calculation pending due to missing emission factor]

### 3.22.17 Case Study / Reference Application

Similar measures are commonly implemented in comparable industrial utility/process systems after site-specific engineering validation. Project-specific case evidence shall be updated after implementation or vendor confirmation.

### 3.22.18 Project Conclusion

This project is technically feasible and financially attractive for implementation. The proposed intervention will reduce annual energy consumption by approximately 1,68,936 kWh, resulting in annual cost saving of ₹12,11,273. With an estimated investment of ₹50,000, the simple payback period is expected to be 0.04 years. Considering the energy saving, operational improvement and sustainability benefits, this project is recommended for implementation under [priority].

# Chapter 4: Annexures

## 4.1 Uploaded Data Sources

Uploaded spreadsheets, measurements, and supporting documents used for this report are referenced here.

## 4.2 Assumptions

Savings, investment, and implementation assumptions are based on the data made available during the audit and SEE-Tech engineering judgment where direct readings were not available.

## 4.3 Image / Figure References

Photographs, schematics, and reference figures included in the report are listed in this section.

## 4.4 Calculation Notes

Calculation notes, formulas, and validation references supporting the ECM analysis are documented here.