SEE-Tech Solutions

Commercial Building Energy Audit Report Format

Detailed Energy Audit Report

Purpose: To identify implementable energy-saving projects with clear investment, savings, payback and execution roadmap.

| Prepared For | MTL Baddi |
| --- | --- |
| Building Type | Industrial Facility |
| Location | Baddi |
| Audit Period | Jan 2025 |
| Report Date | 2025-01-31 |
| Prepared By | SEE-Tech Solutions |
| Document Version | Draft |

# Table of Contents

Chapter 1. Executive Summary

Chapter 2. Plant / Building Details and Energy Profile

Chapter 3. Energy Saving Projects

3.1 GR-1 Cooling System Performance Improvement

ECM 1 � EE Improvement in Chiller Using CT Segregation

ECM 2 � Flow Optimization for CHW Secondary Pump

ECM 3 � EE Improvement in Air Compressors & Pump Using CT Segregation

ECM 4 � Automatic Primary Pump Flow Control for Chiller kW/TR Optimization

ECM 5 � Free Cooling by Chiller Bypass in Winter

ECM 8 � IE5 Efficiency Motor Retrofit for CHW Secondary Pump

ECM 9 � IE5 Efficiency Motor Retrofit for CT Water Secondary Pump

3.2 GR-2 Production Machines

ECM 13 � Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers

ECM 14 � Insulation hot flexible ducts (72 Nos)

ECM 15 � Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos)

ECM 16 � ASB 70 DPH (7 Nos) Servo Motor Project

ECM 17 � ASB 50 MB (18 Nos) Servo Motor Project

ECM 18 � EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project

ECM 19 � EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project

ECM 20 � EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project

3.3 GR-3 Air Compressors

ECM 21 � Compressed Air Measurement & Management

ECM 22 � Booster Compressor retrofit with IE5 Efficiency motor & automation

3.4 GR-4 Auxiliary Systems & Machine Improvement

ECM 6 � CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit

ECM 7 � Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans

ECM 10 � Cutting Grinders Retrofit with IE5 Motor & Cogged belt

ECM 11 � PD blower Direct Mounting with IE5 motor with existing VFD

ECM 12 � APFC relay for 600 kVAr Panel

Chapter 4. Annexures

# Chapter 1: Executive Summary

## 1.1 Purpose of the Energy Audit

Data required

## 1.2 Overall Energy Saving Potential

| Particular | Value |
| --- | --- |
| Total annual electricity consumption | Data required |
| Annual electricity cost | INR 0 |
| Average electricity tariff considered | Data required |
| Number of projects identified | 22 |
| Total energy saving potential | 1902386.6464 |
| Total annual cost saving potential | INR 1,36,40,112 |
| Total estimated investment | INR 2,49,43,149 |
| Simple payback period | 1.83 |
| CO2 reduction potential | Data required |

## 1.3 Summary of Identified Energy Saving Projects

| Project No. | Energy Saving Project | System | Investment INR | Annual Saving INR/year | Energy Saving kWh/year |
| --- | --- | --- | --- | --- | --- |
| ECM 1 | EE Improvement in Chiller Using CT Segregation | Utility | INR 3,50,000 | INR 2,30,355 | 32127.6 |
| ECM 2 | Flow Optimization for CHW Secondary Pump | Utility | INR 1,50,000 | INR 1,27,102 | 17726.85 |
| ECM 3 | EE Improvement in Air Compressors & Pump Using CT Segregation | Utility | INR 4,50,000 | INR 10,34,106 | 144226.71 |
| ECM 4 | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization | Utility | INR 1,45,000 | INR 3,28,615 | 45831.9 |
| ECM 5 | Free Cooling by Chiller Bypass in Winter | Utilty | INR 5,00,000 | INR 4,30,200 | 60000 |
| ECM 6 | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit | Utility | INR 4,88,750 | INR 1,76,561 | 24624.9 |
| ECM 7 | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans | Utility | INR 3,10,000 | INR 1,40,543 | 19601.6 |
| ECM 8 | IE5 Efficiency Motor Retrofit for CHW Secondary Pump | Utility | INR 2,70,000 | INR 1,83,665 | 25615.8 |
| ECM 9 | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump | Utility | INR 10,11,933 | INR 3,74,832 | 52277.82 |
| ECM 10 | Cutting Grinders Retrofit with IE5 Motor & Cogged belt | Process | INR 4,88,599 | INR 2,00,760 | 28000 |
| ECM 11 | PD blower Direct Mounting with IE5 motor with existing VFD | Process | INR 2,70,000 | INR 1,24,220 | 17325 |
| ECM 12 | APFC relay for 600 kVAr Panel | Utility | INR 50,000 | INR 12,11,273 | 168936.3 |
| ECM 13 | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers | ISBM | INR 10,50,000 | INR 3,92,342 | 54720 |
| ECM 14 | Insulation hot flexible ducts (72 Nos) | ISBM | INR 7,40,000 | INR 14,32,566 | 199800 |
| ECM 15 | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) | ISBM | INR 8,50,000 | INR 2,81,064 | 39200 |
| ECM 16 | ASB 70 DPH (7 Nos) Servo Motor Project | ISBM | INR 52,50,000 | INR 19,39,535 | 270506.95 |
| ECM 17 | ASB 50 MB (18 Nos) Servo Motor Project | ISBM | INR 90,00,000 | INR 30,55,386 | 426134.772 |
| ECM 18 | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project | EBM | INR 10,00,000 | INR 3,44,075 | 47988.15 |
| ECM 19 | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project | EBM | INR 6,00,000 | INR 2,01,857 | 28153.048 |
| ECM 20 | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project | EBM | INR 9,10,000 | INR 2,71,590 | 37878.6464 |
| ECM 21 | Compressed Air Measurement & Management | Utility | INR 8,00,000 | INR 10,54,166 | 147024.6 |
| ECM 22 | Booster Compressor retrofit with IE5 Efficiency motor & automation | Utility | INR 2,58,868 | INR 1,05,299 | 14686 |

## 1.4 Category-wise Summary

| Category | No. of Projects | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| GR-1 Cooling System Performance Improvement | 7 | INR 28,76,933 | INR 27,08,874 | 377806.67999999993 | 1.06 |
| GR-2 Production Machines | 8 | INR 1,94,00,000 | INR 79,18,416 | 1104381.5664 | 2.45 |
| GR-3 Air Compressors | 2 | INR 10,58,868 | INR 11,59,465 | 161710.6 | 0.91 |
| GR-4 Auxiliary Systems & Machine Improvement | 5 | INR 16,07,349 | INR 18,53,358 | 258487.8 | 0.87 |

## 1.5 Key Observations

Data required

## 1.6 Conclusion and Way Forward

Based on the audit findings, SEE-Tech recommends that MTL Baddi should proceed with detailed implementation planning for the identified energy-saving projects.

| Step | Action |
| --- | --- |
| Data required | Data required |

# Chapter 2: Plant / Building Details and Energy Profile

## 2.1 General Information

| Name of facility | MTL Baddi Plant |
| --- | --- |
| Address | Baddi |
| Type of building | Industrial Facility |
| Operating days and hours | Data required |
| Facility contact person | Site Team |

## 2.2 Utility and Energy Sources

| Energy Source | Use | Annual Consumption | Annual Cost INR |
| --- | --- | --- | --- |
| Grid electricity | Main electrical loads | Data required | Data required |
| Diesel | DG backup | Data required | Data required |

| Supply voltage | Data required |
| --- | --- |
| Tariff category | Data required |
| Contract demand / sanctioned load | Data required |
| Average electricity tariff | INR/kWh |

## 2.3 Major Energy Consuming Systems

| System | Major Equipment | Estimated Share | Remarks |
| --- | --- | --- | --- |
| Cooling system | Chiller / pumps / cooling tower | Data required | Data required |
| Production machines | Dryers / heaters / servo systems | Data required | Data required |
| Compressed air | Compressors / boosters | Data required | Data required |

## 2.4 Audit Observations

| Annual electricity consumption | Data required |
| --- | --- |
| Specific energy consumption | Data required |
| Reference / target benchmark | Data required |
| Improvement potential | Data required |

| Observation | Impact | Recommendation |
| --- | --- | --- |
| Optimization opportunities exist across major systems. | Higher than necessary energy consumption | Implement ECMs in a phased manner. |

# Chapter 3: Energy Saving Projects

This chapter presents the identified energy conservation measures grouped by system and application area. Each group includes a summary table followed by detailed ECM descriptions.

## 3.1 GR-1 Cooling System Performance Improvement

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 1 | EE Improvement in Chiller Using CT Segregation | INR 3,50,000 | INR 2,30,355 | 32127.6 | 1.519394691 |
| ECM 2 | Flow Optimization for CHW Secondary Pump | INR 1,50,000 | INR 1,27,102 | 17726.85 | 1.180159029 |
| ECM 3 | EE Improvement in Air Compressors & Pump Using CT Segregation | INR 4,50,000 | INR 10,34,106 | 144226.71 | 0.4351586906 |
| ECM 4 | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization | INR 1,45,000 | INR 3,28,615 | 45831.9 | 0.4412462067 |
| ECM 5 | Free Cooling by Chiller Bypass in Winter | INR 5,00,000 | INR 4,30,200 | 60000 | 1.162250116 |
| ECM 8 | IE5 Efficiency Motor Retrofit for CHW Secondary Pump | INR 2,70,000 | INR 1,83,665 | 25615.8 | 1.470065497 |
| ECM 9 | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump | INR 10,11,933 | INR 3,74,832 | 52277.82 | 2.699697685 |

### ECM 1 � EE Improvement in Chiller Using CT Segregation

| Project title | EE Improvement in Chiller Using CT Segregation |
| --- | --- |
| Project number | ECM 1 |
| System | Utility |
| Location | Data required |
| Equipment covered | Chiller (1 No.) |
| Proposed intervention | EE Improvement in Chiller Using CT Segregation |
| Expected energy saving | 32127.6 |
| Expected annual cost saving | INR 2,30,355 |
| Estimated investment | INR 3,50,000 |
| Simple payback period | 1.519394691 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 32127.6 |
| Annual cost saving | ₹/year | 230354.892 |
| Estimated investment | ₹ | 350000 |
| Simple payback | years | 1.519394691 |

### ECM 2 � Flow Optimization for CHW Secondary Pump

| Project title | Flow Optimization for CHW Secondary Pump |
| --- | --- |
| Project number | ECM 2 |
| System | Utility |
| Location | Data required |
| Equipment covered | Chilled Water Secondary Pump (2 Nos) |
| Proposed intervention | Flow Optimization for CHW Secondary Pump |
| Expected energy saving | 17726.85 |
| Expected annual cost saving | INR 1,27,102 |
| Estimated investment | INR 1,50,000 |
| Simple payback period | 1.180159029 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 17726.85 |
| Annual cost saving | ₹/year | 127101.5145 |
| Estimated investment | ₹ | 150000 |
| Simple payback | years | 1.180159029 |

### ECM 3 � EE Improvement in Air Compressors & Pump Using CT Segregation

| Project title | EE Improvement in Air Compressors & Pump Using CT Segregation |
| --- | --- |
| Project number | ECM 3 |
| System | Utility |
| Location | Data required |
| Equipment covered | CT Water Secondary Pump (3 Nos) |
| Proposed intervention | EE Improvement in Air Compressors & Pump Using CT Segregation |
| Expected energy saving | 144226.71 |
| Expected annual cost saving | INR 10,34,106 |
| Estimated investment | INR 4,50,000 |
| Simple payback period | 0.4351586906 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 144226.71 |
| Annual cost saving | ₹/year | 1034105.511 |
| Estimated investment | ₹ | 450000 |
| Simple payback | years | 0.4351586906 |

### ECM 4 � Automatic Primary Pump Flow Control for Chiller kW/TR Optimization

| Project title | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization |
| --- | --- |
| Project number | ECM 4 |
| System | Utility |
| Location | Data required |
| Equipment covered | Chiller |
| Proposed intervention | Automatic Primary Pump Flow Control for Chiller kW/TR Optimization |
| Expected energy saving | 45831.9 |
| Expected annual cost saving | INR 3,28,615 |
| Estimated investment | INR 1,45,000 |
| Simple payback period | 0.4412462067 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 45831.9 |
| Annual cost saving | ₹/year | 328614.723 |
| Estimated investment | ₹ | 145000 |
| Simple payback | years | 0.4412462067 |

### ECM 5 � Free Cooling by Chiller Bypass in Winter

| Project title | Free Cooling by Chiller Bypass in Winter |
| --- | --- |
| Project number | ECM 5 |
| System | Utilty |
| Location | Data required |
| Equipment covered | Chiller |
| Proposed intervention | Free Cooling by Chiller Bypass in Winter |
| Expected energy saving | 60000 |
| Expected annual cost saving | INR 4,30,200 |
| Estimated investment | INR 5,00,000 |
| Simple payback period | 1.162250116 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 60000 |
| Annual cost saving | ₹/year | 430200 |
| Estimated investment | ₹ | 500000 |
| Simple payback | years | 1.162250116 |

### ECM 8 � IE5 Efficiency Motor Retrofit for CHW Secondary Pump

| Project title | IE5 Efficiency Motor Retrofit for CHW Secondary Pump |
| --- | --- |
| Project number | ECM 8 |
| System | Utility |
| Location | Data required |
| Equipment covered | Chilled Water Secondary Pump No. 3 |
| Proposed intervention | IE5 Efficiency Motor Retrofit for CHW Secondary Pump |
| Expected energy saving | 25615.8 |
| Expected annual cost saving | INR 1,83,665 |
| Estimated investment | INR 2,70,000 |
| Simple payback period | 1.470065497 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 25615.8 |
| Annual cost saving | ₹/year | 183665.286 |
| Estimated investment | ₹ | 270000 |
| Simple payback | years | 1.470065497 |

### ECM 9 � IE5 Efficiency Motor Retrofit for CT Water Secondary Pump

| Project title | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump |
| --- | --- |
| Project number | ECM 9 |
| System | Utility |
| Location | Data required |
| Equipment covered | CT Secondary Pump No. 1, 2 & 3 |
| Proposed intervention | IE5 Efficiency Motor Retrofit for CT Water Secondary Pump |
| Expected energy saving | 52277.82 |
| Expected annual cost saving | INR 3,74,832 |
| Estimated investment | INR 10,11,933 |
| Simple payback period | 2.699697685 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 52277.82 |
| Annual cost saving | ₹/year | 374831.9694 |
| Estimated investment | ₹ | 1011933 |
| Simple payback | years | 2.699697685 |

## 3.2 GR-2 Production Machines

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 13 | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers | INR 10,50,000 | INR 3,92,342 | 54720 | 2.67623382 |
| ECM 14 | Insulation hot flexible ducts (72 Nos) | INR 7,40,000 | INR 14,32,566 | 199800 | 0.5165556072 |
| ECM 15 | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) | INR 8,50,000 | INR 2,81,064 | 39200 | 3.024222241 |
| ECM 16 | ASB 70 DPH (7 Nos) Servo Motor Project | INR 52,50,000 | INR 19,39,535 | 270506.95 | 2.706834605 |
| ECM 17 | ASB 50 MB (18 Nos) Servo Motor Project | INR 90,00,000 | INR 30,55,386 | 426134.772 | 2.945617697 |
| ECM 18 | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project | INR 10,00,000 | INR 3,44,075 | 47988.15 | 2.906342794 |
| ECM 19 | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project | INR 6,00,000 | INR 2,01,857 | 28153.048 | 2.972396039 |
| ECM 20 | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project | INR 9,10,000 | INR 2,71,590 | 37878.6464 | 3.35064013 |

### ECM 13 � Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers

| Project title | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers |
| --- | --- |
| Project number | ECM 13 |
| System | ISBM |
| Location | Data required |
| Equipment covered | ASB 70 DPH (8) Dryer |
| Proposed intervention | Energy Saving through Exhaust Heat Recovery in ASB 70 DPH Dryers |
| Expected energy saving | 54720 |
| Expected annual cost saving | INR 3,92,342 |
| Estimated investment | INR 10,50,000 |
| Simple payback period | 2.67623382 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 54720 |
| Annual cost saving | ₹/year | 392342.4 |
| Estimated investment | ₹ | 1050000 |
| Simple payback | years | 2.67623382 |

### ECM 14 � Insulation hot flexible ducts (72 Nos)

| Project title | Insulation hot flexible ducts (72 Nos) |
| --- | --- |
| Project number | ECM 14 |
| System | ISBM |
| Location | Data required |
| Equipment covered | ASB 70 DPH (11), 12M (8), 50 MB (18) : 2 ducts per machine |
| Proposed intervention | Insulation hot flexible ducts (72 Nos) |
| Expected energy saving | 199800 |
| Expected annual cost saving | INR 14,32,566 |
| Estimated investment | INR 7,40,000 |
| Simple payback period | 0.5165556072 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 199800 |
| Annual cost saving | ₹/year | 1432566 |
| Estimated investment | ₹ | 740000 |
| Simple payback | years | 0.5165556072 |

### ECM 15 � Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos)

| Project title | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) |
| --- | --- |
| Project number | ECM 15 |
| System | ISBM |
| Location | Data required |
| Equipment covered | ASB 70 DPH (8) Machine |
| Proposed intervention | Replacement of Band Heater with IR heaters of Barrel Heating (8 Nos) |
| Expected energy saving | 39200 |
| Expected annual cost saving | INR 2,81,064 |
| Estimated investment | INR 8,50,000 |
| Simple payback period | 3.024222241 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 39200 |
| Annual cost saving | ₹/year | 281064 |
| Estimated investment | ₹ | 850000 |
| Simple payback | years | 3.024222241 |

### ECM 16 � ASB 70 DPH (7 Nos) Servo Motor Project

| Project title | ASB 70 DPH (7 Nos) Servo Motor Project |
| --- | --- |
| Project number | ECM 16 |
| System | ISBM |
| Location | Data required |
| Equipment covered | ASB 70 DPH (7) Machines |
| Proposed intervention | ASB 70 DPH (7 Nos) Servo Motor Project |
| Expected energy saving | 270506.95 |
| Expected annual cost saving | INR 19,39,535 |
| Estimated investment | INR 52,50,000 |
| Simple payback period | 2.706834605 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 270506.95 |
| Annual cost saving | ₹/year | 1939534.832 |
| Estimated investment | ₹ | 5250000 |
| Simple payback | years | 2.706834605 |

### ECM 17 � ASB 50 MB (18 Nos) Servo Motor Project

| Project title | ASB 50 MB (18 Nos) Servo Motor Project |
| --- | --- |
| Project number | ECM 17 |
| System | ISBM |
| Location | Data required |
| Equipment covered | ASB 50MB (18 Machines) |
| Proposed intervention | ASB 50 MB (18 Nos) Servo Motor Project |
| Expected energy saving | 426134.772 |
| Expected annual cost saving | INR 30,55,386 |
| Estimated investment | INR 90,00,000 |
| Simple payback period | 2.945617697 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 426134.772 |
| Annual cost saving | ₹/year | 3055386.315 |
| Estimated investment | ₹ | 9000000 |
| Simple payback | years | 2.945617697 |

### ECM 18 � EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project

| Project title | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project |
| --- | --- |
| Project number | ECM 18 |
| System | EBM |
| Location | Data required |
| Equipment covered | EBM CMP Old Machines (5 Nos) |
| Proposed intervention | EBM CMP old 7.5 kW each (5 Nos) Servo Motor Project |
| Expected energy saving | 47988.15 |
| Expected annual cost saving | INR 3,44,075 |
| Estimated investment | INR 10,00,000 |
| Simple payback period | 2.906342794 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 47988.15 |
| Annual cost saving | ₹/year | 344075.0355 |
| Estimated investment | ₹ | 1000000 |
| Simple payback | years | 2.906342794 |

### ECM 19 � EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project

| Project title | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project |
| --- | --- |
| Project number | ECM 19 |
| System | EBM |
| Location | Data required |
| Equipment covered | EBM CMP Old Machines |
| Proposed intervention | EBM CMP old 5.5 kW each (4 Nos) Servo Motor Project |
| Expected energy saving | 28153.048 |
| Expected annual cost saving | INR 2,01,857 |
| Estimated investment | INR 6,00,000 |
| Simple payback period | 2.972396039 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 28153.048 |
| Annual cost saving | ₹/year | 201857.3542 |
| Estimated investment | ₹ | 600000 |
| Simple payback | years | 2.972396039 |

### ECM 20 � EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project

| Project title | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project |
| --- | --- |
| Project number | ECM 20 |
| System | EBM |
| Location | Data required |
| Equipment covered | EBM CMP Old Machines |
| Proposed intervention | EBM CMP old 3.7 kW each (7 Nos) Servo Motor Project |
| Expected energy saving | 37878.6464 |
| Expected annual cost saving | INR 2,71,590 |
| Estimated investment | INR 9,10,000 |
| Simple payback period | 3.35064013 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 37878.6464 |
| Annual cost saving | ₹/year | 271589.8947 |
| Estimated investment | ₹ | 910000 |
| Simple payback | years | 3.35064013 |

## 3.3 GR-3 Air Compressors

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 21 | Compressed Air Measurement & Management | INR 8,00,000 | INR 10,54,166 | 147024.6 | 0.7588934856 |
| ECM 22 | Booster Compressor retrofit with IE5 Efficiency motor & automation | INR 2,58,868 | INR 1,05,299 | 14686 | 2.458414935 |

### ECM 21 � Compressed Air Measurement & Management

| Project title | Compressed Air Measurement & Management |
| --- | --- |
| Project number | ECM 21 |
| System | Utility |
| Location | Data required |
| Equipment covered | Air Compressors (4 Nos: 1 LP, 3 HP) |
| Proposed intervention | Compressed Air Measurement & Management |
| Expected energy saving | 147024.6 |
| Expected annual cost saving | INR 10,54,166 |
| Estimated investment | INR 8,00,000 |
| Simple payback period | 0.7588934856 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 147024.6 |
| Annual cost saving | ₹/year | 1054166.382 |
| Estimated investment | ₹ | 800000 |
| Simple payback | years | 0.7588934856 |

### ECM 22 � Booster Compressor retrofit with IE5 Efficiency motor & automation

| Project title | Booster Compressor retrofit with IE5 Efficiency motor & automation |
| --- | --- |
| Project number | ECM 22 |
| System | Utility |
| Location | Data required |
| Equipment covered | HP Booster Compressor |
| Proposed intervention | Booster Compressor retrofit with IE5 Efficiency motor & automation |
| Expected energy saving | 14686 |
| Expected annual cost saving | INR 1,05,299 |
| Estimated investment | INR 2,58,868 |
| Simple payback period | 2.458414935 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 14686 |
| Annual cost saving | ₹/year | 105298.62 |
| Estimated investment | ₹ | 258867.7 |
| Simple payback | years | 2.458414935 |

## 3.4 GR-4 Auxiliary Systems & Machine Improvement

| ECM No. | ECM Name | Investment INR | Annual Saving INR/year | Energy Saving kWh/year | Payback |
| --- | --- | --- | --- | --- | --- |
| ECM 6 | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit | INR 4,88,750 | INR 1,76,561 | 24624.9 | 2.768172432 |
| ECM 7 | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans | INR 3,10,000 | INR 1,40,543 | 19601.6 | 2.205723223 |
| ECM 10 | Cutting Grinders Retrofit with IE5 Motor & Cogged belt | INR 4,88,599 | INR 2,00,760 | 28000 | 2.433745517 |
| ECM 11 | PD blower Direct Mounting with IE5 motor with existing VFD | INR 2,70,000 | INR 1,24,220 | 17325 | 2.173558659 |
| ECM 12 | APFC relay for 600 kVAr Panel | INR 50,000 | INR 12,11,273 | 168936.3 | 0.0412788767 |

### ECM 6 � CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit

| Project title | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit |
| --- | --- |
| Project number | ECM 6 |
| System | Utility |
| Location | Data required |
| Equipment covered | Cooling Tower Fan Motor, Its Mounting & Blades |
| Proposed intervention | CT No. 2 Fan System Efficiency Upgrade: PMSM Motor + Direct-Mount Fan Retrofit |
| Expected energy saving | 24624.9 |
| Expected annual cost saving | INR 1,76,561 |
| Estimated investment | INR 4,88,750 |
| Simple payback period | 2.768172432 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 24624.9 |
| Annual cost saving | ₹/year | 176560.533 |
| Estimated investment | ₹ | 488750 |
| Simple payback | years | 2.768172432 |

### ECM 7 � Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans

| Project title | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans |
| --- | --- |
| Project number | ECM 7 |
| System | Utility |
| Location | Data required |
| Equipment covered | AHUs (Blower + Motor Change) |
| Proposed intervention | Energy Optimization of Clean Room and IM AHUs Using High-Efficiency Plug Fans |
| Expected energy saving | 19601.6 |
| Expected annual cost saving | INR 1,40,543 |
| Estimated investment | INR 3,10,000 |
| Simple payback period | 2.205723223 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 19601.6 |
| Annual cost saving | ₹/year | 140543.472 |
| Estimated investment | ₹ | 310000 |
| Simple payback | years | 2.205723223 |

### ECM 10 � Cutting Grinders Retrofit with IE5 Motor & Cogged belt

| Project title | Cutting Grinders Retrofit with IE5 Motor & Cogged belt |
| --- | --- |
| Project number | ECM 10 |
| System | Process |
| Location | Data required |
| Equipment covered | Cutting Grinders |
| Proposed intervention | Cutting Grinders Retrofit with IE5 Motor & Cogged belt |
| Expected energy saving | 28000 |
| Expected annual cost saving | INR 2,00,760 |
| Estimated investment | INR 4,88,599 |
| Simple payback period | 2.433745517 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 28000 |
| Annual cost saving | ₹/year | 200760 |
| Estimated investment | ₹ | 488598.75 |
| Simple payback | years | 2.433745517 |

### ECM 11 � PD blower Direct Mounting with IE5 motor with existing VFD

| Project title | PD blower Direct Mounting with IE5 motor with existing VFD |
| --- | --- |
| Project number | ECM 11 |
| System | Process |
| Location | Data required |
| Equipment covered | PD Blower |
| Proposed intervention | PD blower Direct Mounting with IE5 motor with existing VFD |
| Expected energy saving | 17325 |
| Expected annual cost saving | INR 1,24,220 |
| Estimated investment | INR 2,70,000 |
| Simple payback period | 2.173558659 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 17325 |
| Annual cost saving | ₹/year | 124220.25 |
| Estimated investment | ₹ | 270000 |
| Simple payback | years | 2.173558659 |

### ECM 12 � APFC relay for 600 kVAr Panel

| Project title | APFC relay for 600 kVAr Panel |
| --- | --- |
| Project number | ECM 12 |
| System | Utility |
| Location | Data required |
| Equipment covered | APFC |
| Proposed intervention | APFC relay for 600 kVAr Panel |
| Expected energy saving | 168936.3 |
| Expected annual cost saving | INR 12,11,273 |
| Estimated investment | INR 50,000 |
| Simple payback period | 0.0412788767 |

Data required

| Parameter | Unit | Value |
| --- | --- | --- |
| Annual energy saving | kWh/year | 168936.3 |
| Annual cost saving | ₹/year | 1211273.271 |
| Estimated investment | ₹ | 50000 |
| Simple payback | years | 0.0412788767 |

# Chapter 4: Annexures

## 4.1 Uploaded Data Sources

Uploaded spreadsheets, measurements, and supporting documents used for this report are referenced here.

## 4.2 Assumptions

Savings, investment, and implementation assumptions are based on the data made available during the audit and SEE-Tech engineering judgment where direct readings were not available.

## 4.3 Image / Figure References

Photographs, schematics, and reference figures included in the report are listed in this section.

## 4.4 Calculation Notes

Calculation notes, formulas, and validation references supporting the ECM analysis are documented here.